## Intro
| B44-10 | Section 8.7
| Sheet Tab | Alterations
| Electric - 8.7.2 | Alterations to Electric Elevators
| Hydraulic - 8.7.3 | Alterations to Hydraulic Elevators
| Other - 8.7.4 | Alterations to Elevators with Other Types of Driving Machines
| Special - 8.7.5 | Alterations to Special Application Elevators
| Escalator - 8.7.6.1 | Alterations to Escalators
| M-Walk - 8.7.6.2 | Alterations to Moving Walks
| DW & Mat'l Lifts 8.7.7 | Alterations to Dumbwaiters and Material Lifts
1. Select the appropriate Sheet tab (below) depending on the device type that is being altered. 2. Find the appropriate Section heading (column 2 ) which is relevant to the alteration. 3. Expand the Sections using the '+' symbol (at the left of the screen) to reveal the applicable alteration requirements. Note 1: To open (expand) a section select the '+' which is ONE LINE Below the Alteration description. Note 2: Applicable code requirements when expanded are shown on YELLOW background. 4. Collapse the Sections using the '-' symbol (at the left of the screen) that are not relevant to the alteration. 5. Mark with an 'X' the 8.7 item and also those which require compliance checking that are relevant to the alteration. 6. Print the Applicable pages and submit with the Alteration Spec Sheet Package. Non-relevant 8.7 items may be omitted when printing and are not required with the submission.

## 251-12 FULL LISTING
0 | 1 | 2a | 2b | 2c | 3 | 4 | 5 | 6
Conforms to B44 Mark with 'X' | B44-10 Reference Number | Alteration Checklist for Director's Guideline 251-11-r2 Scope of Alteration - B44 - 2010 as amended by CAD 261/13-r1 Part, Section or Requirement |  |  | Type of Alteration Work
[5 empty] | Alteration |  | Replacement with
[5 empty] | Modification Change | Addition | Same | Different Make/Model
|  | Job Reference: |  |  | Type of Submission Required
| 8.7.1.2 | Alterations not specifically covered in 8.7
|  |  | 1.2 | Level of safety shall not be diminished
| 8.7.1.4 | Welding
|  |  | 8.8 | Welding
|  |  | 8.7.1.5 | Design / Weld Engineer
| 8.7.1.7 | Repairs and Replacements
|  |  | 8.6.2 | for repairs
|  |  | 8.6.3 | for replacements
| 8.7.2 | Alterations to Electric Elevators
| 8.7.2.1 | Hoistway Enclosures |  |  | Major | Major
| 8.7.2.1.1 | Hoistway Enclosure Walls |  |  | Major | Major
|  |  | 2.1.1 | Hoistway Enclosures
|  |  | 2.1.5 | Windows and Skylights
|  |  | 2.1.6 | Projections, Recesses, and Setbacks in H/W
|  |  | 2.5. | Horizontal Car and Counterweight Clearances
|  |  | 2.7.3.4.6 | Access Doors and Openings
|  | « | 2.7.3.4.7 | Access Doors and Openings
|  |  | 2.8. | Equipment in Hoistways,Machinery Spaces, Machine Rooms, Control Spaces, and Control Rooms
|  |  | 8.7.2.10 | Entrances and Hoistway Openings (if change includes an entrance)
|  |  | 2.11.1 | Entrances and Emergency Doors Required (if blind H/W)
| 8.7.2.1.2 | Addition of Elevator to Existing Hoistway |  |  | - | New
|  |  | B44-2010 | New Installation
|  |  | 2.5. | Horizontal Car and Counterweight Clearances
| 8.7.2.1.3 | Construction at Top of Hoistway |  |  | Major | Major
|  |  | 2.1.2.1 | Construction at Top of the Hoistway
|  |  | 2.1.3 | Floor Over Hoistways
|  |  | 8.7.2.4 | Vertical Car & Cwt Clearances & Runbys
| 8.7.2.1.4 | Construction at Bottom of Hoistway |  |  | Major | Major
|  |  | 2.1.2.2 | Construction at Bottom of the Hoistway
|  |  | 2.1.2.3 | Strength of Pit Floor
|  |  | 2.2. | Pits
|  |  | 8.7.2.4 | Vertical Car & Cwt Clearances & Runbys
| 8.7.2.1.5 | Control of Smoke and Hot Gases |  |  | Major | Major
|  |  | 2.1.4 | Control of Smoke and Hot Gases
| 8.7.2.2 | Pits | see other alterations below for non Major Alterations |  | Major | -
|  |  | 2.2. | Pits
|  |  | 2.1.2.3 | Strength of Pit Floor
|  |  | 8.7.2.4 | Vertical Car & Cwt Clearances & Runbys
| 8.7.2.2 | Pit Drains & Sumps |  |  | Minor B | Minor B
|  |  | 2.2.2. | Pit Drains
| 8.7.2.2 | Pit Guards |  |  | Minor B | Minor A
|  |  | 2.2.3 | Guards Between Adjacent Pits
| 8.7.2.2 | Pit Access |  |  | Minor B | Minor A
|  |  | 2.2.4 | Pit Access
| 8.7.2.2 | Pit Illumination |  |  | Minor B | Minor B
|  |  | 2.2.5 | Illumination of Pits
| 8.7.2.2 | Pit Stop Switches |  |  | Minor B | Minor A
|  |  | 2.2.6 | Stop Switches
| 8.7.2.2 | Pit Depth |  |  | Minor B | Minor A
|  |  | 2.2.7 | Minimum Pit Depths Required
| 8.7.2.2 | Access to Underside of Car |  |  | Minor B | Minor A
|  |  | 2.2.8 | Access to Underside of Car
| 8.7.2.3 | Location and Guarding of Counterweights |  |  | Major | Major
|  |  | 2.3. | Location and Guarding of Counterweights
|  |  | 2.5.1.2 | Between Car & Cwt and Cwt Guard
|  |  | 2.6. | Protection of Space below H/W
| 8.7.2.4 | Vertical Car and Counterweight Clearances and Runbys (no reduction allowed) |  |  | Major | -
|  |  | 2.4. | Vertical Clearances & Runbys for Cars & Cwts
|  |  | 8.7.2.17.1 | Increase or Decrease in Rise
|  |  | 8.7.2.17.2 | Increase in Rated Speed
|  |  | 8.7.2.25.2 | Change in Location of Driving Machine
| 8.7.2.5 | Horizontal Car and Counterweight Clearances (no reduction allowed) |  |  | Major | -
|  |  | 2.5. | Horizontal Car and Counterweight Clearances
|  |  | 8.7.2.17.2 | Increase in Rated Speed
| 8.7.2.6 | Protection of Spaces Below Hoistways |  |  | Minor B | Major
|  |  | 2.6. | Protection of Space below H/W
| 8.7.2.7 | Machinery Spaces, Machine Rooms Control Spaces and Control Rooms |  |  | ò See Below ò
| 8.7.2.7.1 | Enclosures - other than specifics of 8.7.2.7.2 to 8.7.2.7.7
|  |  | 2.7. (& 3.7.) | New - Machinery Spaces, Machine Rooms Control Spaces & Control Rooms | - | Major
|  |  | 2.7. (& 3.7.) | Altered- Machinery Spaces, Machine Rooms Control Spaces & Control Rooms | Minor A | -
|  |  | OESC | Electrical Equipment Clearances | Minor B | -
| 8.7.2.7.2 | Means of Access |  |  | Minor B | -
|  |  | 2.7.3.1 | General Requirements
|  |  | 2.7.3.2 | Access Across Roofs
|  |  | 2.7.3.3 | Means of Access
| 8.7.2.7.3 | Access Doors and Openings |  |  | Minor B | Minor B | mrr
|  |  | 2.7.3.4 | Access Doors and Openings
|  |  | 2.7.3.5 | Stop Switch for Machinery Space or Control Spaces
| 8.7.2.7.4 | Headroom (no reduction) |  |  | Minor B | Minor B
|  |  | 2.7.4 | Headroom in Machine Rooms/Spaces, Control Room/Spaces
| 8.7.2.7.5 | Windows and Skylights |  |  | Minor B | Minor B
2.1.5
| 8.7.2.7.6 | Lighting (no reduction) |  |  | Minor B | Minor A
|  |  | 2.7.9.1 | Lighting
| 8.7.2.7.7 | Ventilation |  |  | Minor B | Minor B
|  |  | 2.7.9.2 | Temperature & Humidity
| CAD 8.7.2.7«1 | Addition of Elevator Equipment Guarding |  |  | Minor A (per m/c rm) |  | mrr | mrr
|  | (a) | 2.7.2 | Maintenance Path and Clearance
|  | (b) | 2.7.3.4.2 | Size of doors and openings in cage style enclosures (750x2030)
|  | (c) | 2.10.1 | Guarding of Equipment
|  | (d) |  | openable/removable only with tools
|  | (e) |  | operating/work instruction for accessing equipment
|  | (f) |  | clearances in front of electrical control equipment (1000mm)
or clearance required at time of original control installation
|  | (g) |  | access in front of / space to operate main disconnect (1000mm),
or (750mm) if permitted at time of original installation
|  | (h) |  | Installation by registered contractor
|  | (i) |  | designed to be handled by one person
| 8.7.2.8 | Electrical Equipment, Wiring, Pipes, and Ducts in H/W's &M/C Rooms |  |  | Minor B | Minor B | mrr | Minor B
|  | Installation of New (electrical equipment, wiring, raceways, cables, pipes, ducts) |  |  | - | Minor B
also installation of Monitoring Equipment, HVAC
|  |  | 2.8. | Equipment in Hoistways and Machine Rooms
CSA Labeling (or equivalent)
OESC, CSA C22.1 as required
|  | Alteration of Existing (electrical equipment, wiring, raceways, cables, pipes, ducts…) |  |  | Minor B | -
|  |  | 2.8. | Equipment in Hoistways and Machine Rooms
| 8.7.2.9 | Machinery and Sheave Beams, Supports, and Foundations |  |  | Major | Major
New/Relocated Machinery & Sheave Beams, Supports, Foundation
|  |  | 2.9. | Machinery & Sheave Beams, Supports, Foundation
adequacy of building structure verified by P.Eng.
Building reactions increased by more than 5%
|  |  | 2.9. | Machinery & Sheave Beams, Supports, Foundation
adequacy of building structure verified by P.Eng.
| 8.7.2.10 | Entrances and Hoistway Openings |  |  | Major | Major | see below
| 8.7.2.10.1 | General Requirements |  |  | Major | -
| 8.7.2.10.1(a) | General Requirements - All New Entrances |  |  | Major | - | Major | Major
|  |  | 2.11. | Protection of H/W Openings
|  |  | 2.12. | H/W-Door Locking Devices, Elec. Contacts, H/W Access
|  |  | 2.13. | Power Operation of H/W Doors and Car Doors
|  |  | 2.29.2 | Identification of Floors
| 8.7.2.10.1(b) | General Requirements - New Entrances w/Existing Entrances |  |  | - | Major
|  |  | 2.11.2 | Types of Entrances
|  |  | 2.11.3 | Closing of Hoistway Doors
|  |  | 2.11.4 | Location of Horizontally Sliding or Swinging H/W Doors
|  |  | 2.11.5 | Projection of Entrances & Equip. Beyond Land'g Sills
|  |  | 2.11.6 | Opening of Hoistway Doors
|  |  | 2.11.7 | Glass in Hoistway Doors
|  |  | 2.11.8 | Weights for Closing or Balancing Doors
|  |  | 8.7.2.10.5 | Marking of Entrance Assemblies
Entire installation to meet:
|  |  | 2.11.6 | Opening of Hoistway Doors
|  |  | 2.12. | H/W-Door Locking Devices, Elec. Contacts, H/W Access
|  |  | 2.13. | Power Operation of H/W Doors and Car Doors
|  |  | 2.29.2 | Identification of Floors
| 8.7.2.10.1(c) | General Requirements - Alteration to H/W Entrance |  |  | Major | -
|  |  | 2.11.3 | Closing of Hoistway Doors
|  |  | 2.11.5 | Projection of Entrances & Equip. Beyond Land'g Sills
|  |  | 2.11.7 | Glass in Hoistway Doors
|  |  | 2.11.8 | Weights for Closing or Balancing Doors
|  |  | 8.7.2.10.5 | Marking of Entrance Assemblies
Entire installation to meet:
|  |  | 2.12. | H/W-Door Locking Devices, Elec. Contacts, H/W Access
|  |  | 2.13. | Power Operation of H/W Doors and Car Doors
|  |  | 2.29.2 | Identification of Floors
| 8.7.2.10.1(d) | General Requirements - Emergency Doors (added or altered) |  |  | Major | Major
|  |  | 2.11.1 | Entrances and Emergency Doors Required
|  |  | 8.7.2.10.5 | Marking of Entrance Assemblies
| 8.7.2.10.1(e) | General Requirements - Access Openings (installed for cleaning) |  |  | Major | Major
|  |  | 2.11.1.4 | Access Opening for Cleaning of Car & H/W Enclosure
|  |  | 8.7.2.10.5 | Marking of Entrance Assemblies
| 8.7.2.10.2 | Horizontal Slide-Type Entrances - new entrance and components to meet: |  |  | Major | Major | see below
|  |  | 8.7.2.10.1 | Entrances & H/W Openings - General Req'mts |  |  | Major
|  |  | 2.11.11 | Entrances, Horizontal Slide Type
Installed New components to meet:
| sills (a) |  | 2.11.10.1 | Landing-Sill Guards | Minor B |  | Minor B
|  |  | 2.11.11.1 | Landing Sills
|  |  | 2.11.11.6 | Bottom Guides
| hanger /track (b) |  | 2.11.11.2 | Hanger Tracks, and Track Supports | Minor B |  | Minor B
| frame (c) |  | 2.11.11.3 | Entrance Frames | Minor A |  | Minor A
|  |  | 2.11.11.5.1 | Panel Overlap
|  |  | 2.11.11.5.2 | Panel Gaps Clearances
|  |  | 2.11.11.5.3 | Pockets in Strike Jamb
|  |  | 8.7.2.10.5 | Marking of Entrance Assemblies
| hangers (d) |  | 2.11.11.4 | Hangers | Minor B |  | Minor B
| panels (e) |  | 2.11.11.5(*) | Panels | Minor A |  | Minor A
|  |  | 2.11.11.6 | Bottom Guides
|  |  | 2.11.11.7 | Multipanel Entrances
|  |  | 8.7.2.10.5 | Marking of Entrance Assemblies
| retainers (f) |  | 2.11.11.8 | Hoistway Door Safety Retainers | Minor B |  | Minor B
| 8.7.2.10.3 | Vertical-Slide-Type Entrances - new entrance and components to meet: |  |  | Major | Major | see below
|  |  | 8.7.2.10.1 | Entrances & H/W Openings - General Req'mts |  |  | Major
|  |  | 2.11.12 | Entrances, Vertical Slide Type
Installed New components to meet:
| sills (a) |  | 2.11.10.3 | Hinged Hoistway Landing Sills | Minor B |  | Minor B
|  |  | 2.11.12.1 | Landing Sills
| frames (b) |  | 2.11.12.2 | Entrances Frames | Minor B |  | Minor B
|  |  | 8.7.2.10.5 | Marking of Entrance Assemblies
| rails (c) |  | 2.11.12.3 | Rails | mrr |  | mrr
| panels (d) |  | 2.11.12.3 | Rails | Minor A |  | Minor A
|  |  | 2.11.12.4 | Panels
|  |  | 2.11.12.5 | Guides
|  |  | 2.11.12.6 | Counterweighting or Counterbalancing
|  |  | 2.11.12.8 | Pull Straps
|  |  | 8.7.2.10.5 | Marking of Entrance Assemblies
| guides (e) |  | 2.11.12.5 | Guides | mrr |  | mrr
| sill guard (f) |  | 2.11.12.7 | Sill Guards
| straps (g) |  | 2.11.12.8 | Pull Straps
| 8.7.2.10.4 | Swing-Type Entrances - new entrance and components to meet: |  |  | Major | Major | see below
|  |  | 8.7.2.10.1 | Entrances & H/W Openings - General Req'mts |  |  | Major
|  |  | 2.11.13 | Entrances, Swing Type
Installed New components to meet:
| sills (a) |  | 2.11.10.1 | Landing-Sill Guards | Minor B |  | Minor B
|  |  | 2.11.10.3 | Hinged Hoistway Landing Sills
|  |  | 2.11.13.1 | Landing Sills
| frames (b) |  | 2.11.13.2 | Entrance Frames | Minor B |  | Minor B
|  |  | 2.11.13.4 | Hinges
|  |  | 8.7.2.10.5 | Marking of Entrance Assemblies
| panels (c) |  | 2.11.13.3 | Panels | Minor B |  | Minor B
|  |  | 2.11.13.4 | Hinges
|  |  | 2.11.13.5 | Marking
|  |  | 8.7.2.10.5 | Marking of Entrance Assemblies
| hinges (d) |  | 2.11.13.4 | Hinges | mrr |  | mrr
| 8.7.2.10.5 | Marking of Entrance Assemblies (Alteration to an Entrance Door Panel) |  |  | Major | Major
Fire Protection Rating not less then existing entrance
|  |  | 8.7.2.10.5(a) | NBCC requirements
| CAD 8.7.2.10«1 | « Removing Service To a Floor |  |  | Minor B
Bolt entrances shut
Remove Interlock From Safety String
Remove COP Floor Button
|  |  | 2.11.6.2 | Cannot Lock Out Top/Btm, Designated/Alternate, All Landing in Phase II
|  |  | 2.12.7 | H/W Access Switches - if floor was previously the access location
| CAD 8.7.2.10«2 | « Door Safety Retainers |  |  | Minor B | Minor A | mrr | Minor B
|  |  | 2.11.11.8 | Hoistway Door Safety Retainers
| 8.7.2.11 | Hoistway Door-Locking Devices, Access Switches & Parking Devices |  |  | ò See Below ò
| 8.7.2.11.1 | Interlocks |  |  | - | Major | mrr | Minor B
|  |  | 2.12.1 | General
|  |  | 2.12.2 | Interlocks
|  |  | 2.12.4 | Listing/Certification Locking Devices
|  |  | 2.12.5 | Restricted Opening of H/W or Car Door (n/a for column 5,6) |  |  | n/a
|  |  | 2.12.6 | Hoistway Door Unlocking Devices (n/a for column 5,6) |  |  | n/a
|  |  | 2.12.7 | Hoistway Access Switches (n/a for column 5,6) |  |  | n/a
| 8.7.2.11.2 | Mechanical Locks and Electric Contacts |  |  | - | Major | mrr | Minor B
|  |  | 2.12.1 | General
|  |  | 2.12.3 | H/W Door Combination Mechanical Locks & Contacts
|  |  | 2.12.4 | Listing/Certification Locking Devices
|  |  | 2.12.6 | Hoistway Door Unlocking Devices
| 8.7.2.11.3 | Parking Devices |  |  | Minor A | Minor A
|  |  | 8.7.2.11.3 | requirements specified
| 8.7.2.11.4 | Access Switches and Unlocking Devices
| 8.7.2.11.4 (a) | Addition of Unlocking Devices |  |  | - | Minor B | mrr
|  |  | 2.12.6 | Hoistway Door Unlocking Devices
| 8.7.2.11.4 (b) | Addition of Access Switches |  |  | - | Minor A | mrr
|  |  | 2.12.7 | Hoistway Access Switches
|  |  | 2.26.1.4 | Inspection Operation
| 8.7.2.11.5 | Restricted Opening of H/W or Car Doors of Passenger Elevators (Restrictors) (Altered or Installed) |  |  | Minor B | Minor B | mrr | Minor B
|  |  | 2.12.5 | Restricted Opening of H/W or Car Door
| 8.7.2.12 | Power Operation of Hoistway Doors (Addition / Alteration to Power Open or Close) |  |  | Minor A | Minor A
|  |  | 8.7.2.10.1 | Entrances & H/W Openings - General Req'mts
|  |  | 8.7.2.10.2 | Horizontal Slide-Type Entrances
|  |  | 8.7.2.10.3 | Vertical Slide-Type Entrances
|  |  | 8.7.2.10.5 | Marking of Entrance Assemblies
|  | « | 2.13. | Power Operation of Hoistway Doors and Car Doors
| CAD 8.7.2.12«1 | « Replacement of Door Operator |  |  | - | - | mrr | Minor B
|  |  | 2.13. | Power Operation of Hoistway Doors and Car Doors
8.7.2.15«1,«2
| 8.7.2.13 | Door Reopening Device (Safety Edge) (Altered or Added or replaced) |  |  | Minor B | Minor B | mrr | Minor B
|  |  | 2.13.4 | Closing Limitations for Power Operated HS Doors & Gates |  |  | see
|  |  | 2.13.5 | Reopening Device for Power Operated Car Doors or Gates |  |  | 8.6.3.8
if FEO provided, door opening & closing to PHI &II at time of install
8.7.2.15«1,«2
| 8.7.2.14 | Car Enclosures, Car Doors and Gates, and Car Illumination |  |  | ò See Below ò
| 8.7.2.14.1 | Installation of New Car Enclosure |  |  | Major | -
|  |  | 2.14. | Car: Enclosure, Doors, Gates, Illumination
|  |  | 2.15. | Car Frames & Platforms
|  |  | 2.17 | Car and counterweight safeties
|  |  | 8.7.2.15.1 | Alterations to Car Frames and Platforms
| 8.7.2.14.2 | Alteration to Existing Cars |  |  | Minor A | Minor A
| 8.7.2.14.2(a) | Car Enclosure - Securing of Enclosures |  |  | Minor A | Minor A
|  |  | 2.14.1.2 | Securing of Enclosures
| 8.7.2.14.2(b) | Top Emergency Exit (Altered or Added) |  |  | Minor B | Minor B
|  |  | 2.14.1.5 | Top Emergency Exits
| 8.7.2.14.2(c) | Installation of Glass |  |  | Minor B | Minor B
|  |  | 2.14.1.8 | Glass in Elevator Cars
|  |  | 2.14.1.8.1 | Enclosures include glass
|  |  | 2.14.1.8.2 | Lining of Walls or Ceilings include glass |  |  | mrr
|  |  | 2.14.1.8.3 | Marking of each Glazing Panel
| 8.7.2.14.2(d) | Specific Equipment in Elevator Car |  |  | Minor B | Minor B
|  |  | 2.14.1.9 | Equipment Inside Cars
|  |  | (a) | Handrails
|  |  | (b) | fastening devices for protective linings
|  |  | (c) | ceiling mounted hooks/tracks
|  |  | (d) | picture frames display boards, plaques <38mm protrusion
secured to 2.14.1.2
material to 2.14.2.1
|  |  | (e) | conveyor tracks in freights
|  |  | (f ) | heating or cooling equipment
8.7.2.15«1,«2
| CAD 8.7.2.14«1 | « Car operating station |  |  | Minor B | Minor B | mrr | Minor B
verify inspection operation 'if provided'
verify stop sw
verify switches operate as before (eg. FS, FEO, Access)
8.7.2.15«1,«2
| CAD 8.7.2.14«2 | « video cameras / surveillance equipment / video monitors |  |  | Minor B | Minor B
|  |  | 2.8.2.1 | electrical equipment & wiring
|  |  | 2.14.1.2.3 | securing of enclosure equipment
|  |  | 2.14.2.4 | Headroom in Elevator Cars
8.7.2.15«1,«2
| CAD 8.7.2.14«3 | « other equipment |  |  | Variance
| 8.7.2.14.2(e) | Side Emergency Exits - Secured Shut |  |  | Major | -
| 8.7.2.14.2(f) | Car Ventilation |  |  | Minor B | -
|  |  | 2.14.2.3 | Ventilation
| 8.7.2.14.2(g) | Car Illumination |  |  | Minor B | Minor B
|  |  | 2.14.7 | Illumination of Cars and Lighting Fixtures
| 8.7.2.14.2(h) | Partitions Installed in Elevator Cars |  |  | Major | Major
|  |  | 2.16.1.2 | Use of Partitions for Reducing Inside Net Platform Area
| 8.7.2.14.2(i) | Installation of Car Door or Gate, Installation to meet: |  |  | Major | Major
|  |  | 2.14.4 | Passenger and Freight Car Doors/Gates, General Requirements
|  |  | 2.14.5 | Passenger Car Doors
|  |  | 2.14.6 | Freight Elevator Car Doors and Gates
| 8.7.2.14.4 | Car Enclosure / Car Door or Car Gates |  |  | ò See Below ò
| 8.7.2.14.4 | Alteration to Car Enclosure other than 8.7.2.14.2 - Enclosure Materials
|  |  | 2.14. | Car: Enclosure, Doors, Gates, Illumination
enclosure material flame ratings shall not be diminished
|  |  |  | 2.14.1.7 car top railing - see CAD 8.7.2.14«4 |  | Minor A
|  |  |  | 2.14.7.1.3 auxiliary lighting |  | Minor B
|  |  |  | 2.14.7.1.4 car top light & outlet |  | Minor B
|  | « |  | CAD 8.7.2.15«1 | Minor B |  | Minor B
or
|  | « |  | CAD 8.7.2.15«2 | Minor A |  | Minor A
| 8.7.2.14.4 | Alteration to Car Door or Car Gates other than 8.7.2.14.2 |  |  | Minor A | Minor A
|  |  | 2.14. | Car: Enclosure, Doors, Gates, Illumination
2.14.1.7 car top railing
2.14.7.1.3 auxiliary lighting
2.14.7.1.4 car top light & outlet
| O.Reg.209/01s30 | « Relocation of Elevator License to remote location |  |  | Minor B† | -
| CAD 8.7.2.14«4 | « Car Top Guard Rail |  |  | Minor B | Minor A | - | Minor A
|  | CAD | 8.7.2.14«4(a) | Standard Guardrail (to CAD 8.7.2.14«4(a), 2.14.1.7 & OBC)
or
|  | CAD | 8.7.2.14«4(b) | Foldable Guardrail (to CAD 8.7.2.14«4(b), 2.14.1.7 & OBC)
car top run buttons not enabled until extended
normal operation not enabled until stowed
electrical limits to ensure car top clearance in overhead
minor A submission template
|  |  | 8.7.2.15«1,«2 | car weighed prior to alteration
include testing procedure
include revised electrical schematics
| 8.7.2.15 | Car Frames and Platforms |  |  | ò See Below ò
| 8.7.2.15.1 | Alterations to Car Frames and Platforms |  |  | Major | - | Major
|  |  | 2.15. | Car Frames & Platforms
| CAD 8.7.2.15«1 | « Decrease Deadweight <5% or Increase Deadweight of Car (115 kg or Less) |  |  | Minor B | Minor B
|  | CAD | 8.7.2.15«1(a) | cars weighed prior to alteration
|  | CAD | 8.7.2.15«1(b) | In/Out weights recorded or cars weighed after alteration
|  | CAD | 8.7.2.15«1(c) | weight change recorded on auxilliary data tag
|  | CAD | 8.7.2.15«1(e) | testing prior to operation to ensure security of interior finishes
| CAD 8.7.2.15«2 | « Increase Deadweight of Car (>115 kg to 5%) |  |  | Minor A | Minor A
|  | CAD | 8.7.2.15«1
engineering assessment of related items affected by weight change
| 8.7.2.15.2 | Increase or Decrease in Deadweight of Car (Car Wt+Rated Load> 5%) |  |  | Major | -
|  |  | 2.15.(*) | Car Frames & Platforms - «apron guard to ED CAD/as pit permits
|  |  | 2.15.9 | Platform Guards (Aprons)
|  |  | 2.16. | Capacity & Loading
|  |  | 2.17. | Car & Cwt Safeties
|  |  | 2.18. | Speed Governors
|  |  | 2.20. | Suspension Ropes & Connections
|  |  | 2.21.(*) | Counterweights
|  |  | 2.22.(*) | Buffers & Bumpers
|  |  | 2.23. | Car & Cwt Guides Rails, Guide Rail Support, Fastenings
|  |  | 2.24.(*) | Driving Machines & Sheaves
|  |  | 8.7.2.9 | Machinery and Sheave Beams, Supports, Foundations
|  | CAD | 8.7.2.15«1(a) to (e)
| 8.7.2.16 | Capacity, Loading, and Classification |  |  | Major | -
| 8.7.2.16.1 | Change in Type of Service: Passenger to Freight OR Freight to Passenger |  |  | Major | -
|  |  | 2.11.1 | Entrances and Emergency Doors Required
|  |  | 2.11.2 | Types of Entrances
|  |  | 2.11.3 | Closing of Hoistway Doors
|  |  | 2.11.5 | Projection of Entrances & Equip. Beyond Land'g Sills
|  |  | 2.11.6 | Opening of Hoistway Doors
|  |  | 2.11.7 | Glass in Hoistway Doors
|  |  | 2.11.8 | Weights for Closing or Balancing Doors
|  |  | 2.12. | H/W-Door Locking Devices, Elec. Contacts, H/W Access
|  |  | 2.13. | Power Operation of H/W Doors and Car Doors
|  |  | 2.22 (*) | Buffers & Bumpers
|  |  | 2.14. | Car: Enclosure, Doors, Gates, Illumination
|  |  | 2.14.1.7.1 | car top guard rail to CAD 8.7.2.144
|  |  | 2.15.(*) | Car Frames & Platforms - «apron guard to ED CAD/as pit permits
|  |  | 2.16. | Capacity & Loading
|  |  | 2.17.(*) | Car & Cwt Safeties
|  |  | 2.18.(*) | Speed Governors
|  |  | 2.19. | Ascending Car Overspeed & Unintended Car Movement Protection
|  |  | 2.20. | Suspension Ropes & Connections
|  |  | 2.24.(*) | Driving Machines & Sheaves
|  |  | 2.25. | Terminal Stopping Devices
|  |  | 2.26. | Operating Devices and Control Equipment
|  |  | 2.27. | Emergency Operation & Signaling Devices
2.27.1 Car Emergency Signalling Devices
2.27.2 Emergency or Standby Power Systems
2.27.3 FEO: Automatic Elevators
CAD 2.27.3.2.2
2.27.4 FEO: Non-Automatic Elevators
2.27.5 FEO: Automatic Elevators w/Attendant
2.27.6 FEO: Inspection Operation
2.27.7 FEO: Operating Procedures
2.27.8 Switch Keys
2.27.9 Elevator Corridor Call Station Pictograph if reqd by OBC
| 8.7.2.16.2 | Change in Class of Loading: [from any class to any other class ie A, B, C1, C2, C3] |  |  | Major | -
|  |  | 2.16.2 | Minimum Rated Load for Freight Elevators
|  |  | 8.7.2.16.4 | Increase in Rated Load
| 8.7.2.16.3 | Carrying of Passengers on Freight Elevators |  |  | Major | -
|  |  | 2.16.4 | Carrying of Passengers on Freight Elevators
|  |  | 2.16.4.1 | not accessible to general public
|  |  | 2.16.4.2 | rated load not less than required by 2.16.1
|  |  | 2.16.4.3 | conforms to 2.16.8 Passenger Overload in Down Direction
|  |  | 2.16.4.4 | H/W entrances to 2.12.1.1 & 2.11.2.1 or 2.11.2.2(e)
|  |  | 2.16.4.5 | car doors to 2.14.5 Passenger Car Doors
|  |  | 2.16.4.6 | car enclosure openings to 2.14.2.2 Prohibited Openings
|  |  | 2.16.4.7 | conforms to 2.12.5 Restricted Opening of H/W or Car Door
|  |  | 2.16.4.8 | Fs for suspension ropes to Table 2.20.3
|  |  | 2.16.4.9 | Power Operated vertical doors to 2.13.3.4
|  |  | « | apron guard to ED CAD or extent pit permits
|  |  | « | 2.16.5 Signs Required in Freight Elevator Cars
| 8.7.2.16.4 | Increase in Rated Load |  |  | Major | -
Car doors or gates shall be provided at all car entrances
New Car doors and gates to: 2.14.4, 2.14.5, 2.14.6
|  |  | 2.14.4 | Passenger & Frt Car Doors & Gates, General Req'mts
|  |  | 2.14.5 | Passenger Car Doors
|  |  | 2.14.6 | Freight Elevator Car Doors and Gates
|  |  | 2.15.(*) | Car Frames & Platforms- «apron guard to ED CAD/as pit permits
|  |  | 2.16. | Capacity & Loading
|  |  | 2.17. | Car & Cwt Safeties
|  |  | 2.18.(*) | Speed Governors
|  |  | 2.19. | Ascending Car Overspeed & Unintended Car Movement Protection
|  |  | 2.20. | Suspension Ropes & Connections
|  |  | 2.21.(*) | Counterweights
|  |  | 2.22.(*) | Buffers & Bumpers
|  |  | 2.23. | Car & Cwt Guides Rails, Guide Rail Support, Fastenings
|  |  | 2.24. | Driving Machines & Sheaves
|  |  | 2.26.1.4 | Inspection Operation
|  |  | 2.26.1.5 | Inspection Operation with Open Door Circuits
|  |  | 2.26.5 | Monitor & Prevent Automatic Operation w/ Faulty Door Contacts
|  |  | 8.7.2.9 | Machinery and Sheave Beams, Supports, Foundations
| 8.7.2.17 | Change in Rise or Rated Speed |  |  | Major | -
| 8.7.2.17.1 | Increase or Decrease in Rise |  |  | Major | -
|  |  | 2.25. | Terminal Stopping Devices
retain drum m/c, travel increase < 4570mm
|  |  | 2.4.(*) | Vertical Clearances & Runbys for Cars & Cwts
If decrease in rise is at lowest end then;
2.2.4 Access to Pits
2.2.5 Illumination of Pits
2.2.6 Stop Switches
| 8.7.2.17.2 | Increase in Rated Speed |  |  | Major | -
| 8.7.2.17.2(a) | Increase in Rated Speed on a Winding Drum machine |  |  | Major | -
Increase in Rated Speed of a winding drum m/c prohibited
|  |  | 8.7.2.17.2(c) | except as permitted 8.7.2.17.2(c)
| 8.7.2.17.2(b) | Increase in Rated Speed except as per 8.7.2.17.2(c) |  |  | Major | -
|  |  | 2.4.2 | Minimum Bottom Runby for Counterweighted Elevators
|  |  | 2.4.3 | Minimum Bottom Runby for Uncounterweighted Elevators
|  |  | 2.4.4 | Maximum Bottom Runby
|  |  | 2.4.5 | Counterweight Runby Data Plate
|  |  | 2.4.6 | Maximum Upward Movement of the Car
|  |  | 2.4.7 | Top of Car Clearances
|  |  | 2.4.8 | Top of Counterweight Clearances
|  |  | 2.4.9 | Equipment on Top of Car Not Permitted to Strike O/H
|  |  | 2.5. | Horizontal Car and Counterweight Clearances
Car doors or gates shall be provided at all car entrances
|  |  | 2.14. | New doors/gates to: Car: Enclosure, Doors, Gates, Illumination
|  |  | 2.16. | Capacity & Loading
|  |  | 2.17. | Car & Cwt Safeties
|  |  | 2.18.(*) | Speed Governors
|  |  | 2.19. | Ascending Car Overspeed & Unintended Car Movement Protection
|  |  | 2.20. | Suspension Ropes & Connections
|  |  | 2.21.4.2 | Comp Rope Tie Down (if speed > 3.5 m/s)
|  |  | 2.22.(*) | Buffers & Bumpers
|  |  | 2.24. | Driving Machines & Sheaves
|  |  | 2.25. | Terminal Stopping Devices
|  |  | 2.26.(*) | Operating Devices and Control Equipment
| 8.7.2.17.2(c) | Increase in Rated Speed less than 10% & less than 0.20m/s |  |  | Major | -
new spd <.75 for type A safeties
new spd <1 w/spring buffer, 2.18.2.1&.2
|  |  | 2.18.2.1 | Car speed governors
|  |  | 2.18.2.2 | counterweight speed governors
|  |  | 8.7.2.27.3 | Change in Power Supply
| 8.7.2.17.3 | Decrease in Rated Speed |  |  | Major | -
|  |  | 2.4. | Vertical Clearances & Runbys for Cars & Cwts
|  |  | 2.18.2 | Tripping Speeds for Speed Governors
|  |  | 2.16. | Capacity & Loading
|  |  | 2.16.3(*) | Capacity and Data Plates
|  |  | 2.26.4.1 | Electrical Equipment and Wiring
|  |  | 2.26.4.2 | Drive Machine Controllers for Stopping/Starting/Controlling
|  |  | 2.26.4.3 | Positively Opened Contacts
| 8.7.2.18 | Car and Counterweight Safeties |  |  | Major | Major | òSee Below ò
| 8.7.2.18.1 | New Car Safeties |  |  | - | Major | mrr | Minor A
|  |  | 2.17. | Car & Cwt Safeties
|  |  | 2.18. | Speed Governors
|  |  | 2.23. | Car & Cwt Guides Rails, Guide Rail Support, Fastenings
|  |  | 8.7.2.19 | Speed Governors and Governor Ropes
| 8.7.2.18.2 | New Cwt Safeties |  |  | - | Major | mrr | Minor A
|  |  | 2.17. | Car & Cwt Safeties
|  |  | 2.18. | Speed Governors
|  |  | 2.23. | Car & Cwt Guides Rails, Guide Rail Support, Fastenings
|  |  | 8.7.2.19 | Speed Governors and Governor Ropes
| 8.7.2.18.3 | Existing Car Safeties |  |  | Major | - | mrr | Minor A
|  |  | 2.17.(*) | Car & Cwt Safeties
|  |  | 2.18. | Speed Governors
|  |  | 2.23. | Car & Cwt Guides Rails, Guide Rail Support, Fastenings
|  |  | 8.7.2.19 | Speed Governors and Governor Ropes
| 8.7.2.18.3 | Existing Cwt Safeties |  |  | Major | - | mrr | Minor A
|  |  | 2.17. | Car & Cwt Safeties
|  |  | 2.18. | Speed Governors
|  |  | 2.23. | Car & Cwt Guides Rails, Guide Rail Support, Fastenings
|  |  | 8.7.2.19 | Speed Governors and Governor Ropes
| 8.7.2.19 | Speed Governors and Governor Ropes |  |  | Major | Major | òSee Below ò
| 8.7.2.19 |  | 2.18. | Speed Governors |  |  | mrr | Minor A
see
8.6.3.6
| 8.7.2.19 |  | 2.17.15 | Governor Rope Releasing Carriers |  |  | mrr | mrr
see 8.6.3.9
| 8.7.2.19 |  | Governor Ropes of different material or Construction to: |  |  |  | - | Minor B
2.18.6 Design Gov'r Rope Retarding Means for Type B Safeties
2.18.7 Traction between Speed Governor Rope & Sheave
|  |  | & testing to | 2.17.3 Function and Stopping Distances of Safeties
| 8.7.2.20 | Ascending Car Overspeed and Unintended Car Movement Protection (ACO & UCM) |  |  | Minor A | Major | mrr | Minor A
|  |  | 2.19. | Ascending Car Overspd & Unintended Car Movement Protection
| CAD 8.7.2.20«1 | « | If Elevators Controllers are pre-B44-00 & have ACO & UCM |  | Minor A | - | mrr | Minor A
|  |  | 2.19. | ACO & UCM Protection, Except that;
detection means to B44-M90 or the code at time of install
|  |  | 8.9. | Code Data tag to reflect code at time of install
| CAD 8.7.2.20«2 | « | If Elevators Controllers are pre-B44-00 & have ACO ONLY |  | Minor A | - | mrr | Minor A
|  |  | 2.19.1 | ACO Protection Only, Except that;
|  |  | 2.19.3 | Emergency Brake and
detection means to B44-M90 or the code at time of install
|  |  | 2.19.4 | Emergency Brake Supports
|  |  | 8.9. | Code Data tag to reflect code at time of install
| CAD 8.7.2.20«3 | « | Voluntary Addition of Both ACO and UCM where previously not provided |  |  | Minor A
|  |  | 2.19. | ACO & UCM Protection Except that;
detection means to B44-M90 code or later
|  |  | 2.7. | Machinery Spaces, Machine Rooms Control Spaces & Control Rooms
as applicable to the equipment installation
|  |  | 8.9. | Code Data tag to reflect code edition used for the alteration
| 8.7.2.21 | Suspension Ropes and Their Connections |  |  | ò See Below ò
| 8.7.2.21.1 | Change in Number of, or Diameter of Ropes |  |  | Major | -
|  |  | 2.20. | Suspension Ropes & Connections
PEO to certify existing sheaves w/different ropes are satisfactory
| 8.7.2.21.1 | Change in Material / Grade of Ropes |  |  | Minor A | -
|  |  | 2.20. | Suspension Ropes & Connections
PEO to certify existing sheaves w/different ropes are satisfactory
| 8.7.2.21.2 | Addition of Rope Equalizers |  |  | Minor B | Minor B | See 8.6.3.2
|  |  | 2.20.5 | Suspension Rope Equalizers
| 8.7.2.21.3 | Addition of Auxiliary Rope-Fastening Devices |  |  | Major | Major
|  |  | 2.20. | Suspension Ropes & Connections
| 8.7.2.21.4 (a) | Change in Type of Suspension Means |  |  | Major | Major
|  |  | 2.20.8.1 | Protection Against Traction Loss
|  |  | 2.20.8.2 | Broken Suspension Member
|  |  | 2.20.8.3 | Suspension-Member Residual Strength
|  |  | 2.20.11 | Suspension-Member Test
| 8.7.2.21.4 (b) | Traction Loss Detection |  |  | Minor A | Minor A
|  |  | 2.20.8.1 | Protection Against Traction Loss
| 8.7.2.21.4 (c) | Broken Suspension Means Detection |  |  | Minor A | Minor A
|  |  | 2.20.8.2 | Broken Suspension Member
| 8.7.2.22 | Counterweights |  |  | Minor A | -
| 8.7.2.22.1 |  | Alteration to any part of a cwt except guiding members
|  |  | 2.21. | Counterweights
|  |  | 8.7.2.22.2 | Rod Type Counterweights
|  |  | 8.7.2.3 | Location and Guarding of Counterweights
| 8.7.2.22.2 |  | Rod Type Cwt - can retain if:
Minimum of 2 suspension and 2 tie rods
Suspension rods:
|  |  | 2.21.2.1 | Material - Cwt Frames & Rods
|  |  | 2.21.2.3 | Factor of Safety
Tie Rods:
|  |  | 2.21.1.2 | Retention of Weight Sections
| 8.7.2.22.3 |  | Roller or similar guide shoes added |  | mrr |  | mrr
safety jaws cannot touch rails if not activated
| 8.7.2.23 | Car and Counterweight Buffers and Bumpers |  |  | Major | - | mrr | Minor B
|  |  | 2.22.(*) | Buffers & Bumpers
| 8.7.2.24 | Guide Rails, Supports, and Fastenings (alteration to, or stress increase >5%) |  |  | Major | -
|  |  | 2.23. | Car & Cwt Guides Rails, Guide Rail Support, Fastenings
| 8.7.2.25 | Driving Machines and Sheaves |  |  | ò See Below ò
| 8.7.2.25.1 | Alter / Replace |  | Driving Machines & Sheaves | Major | Major | Major
| 8.7.2.25.1(a) |  |  | Driving Machine Installed as part of an alteration | Major | -
|  |  | 2.7.2 | Maintenance Path and Clearance
to extent existing installation permits
|  |  | 2.9. | Machinery & Sheave Beams, Supports, Foundation
|  |  | 2.10.1 | Guarding of Equipment
|  |  | 2.19. | Ascending Car Overspeed & Unintended Car Movement Protection
|  |  | 8.7.2.20 | ACO & UCM Protection
|  | CAD | 8.7.2.20«1 | Pre B44-00 ACO & UCM Protection
|  | CAD | 8.7.2.20«2 | Pre B44-00 ACO Only Protection
|  | CAD | 8.7.2.20«3 | Addition ACO/UCM if not required by other alteration scope
|  |  | 2.20. | Suspension Ropes & Connections
|  |  | 2.24. | Driving Machines & Sheaves
|  |  | 2.26.8 | Release and Application of Driving-Machine Brakes
| 8.7.2.25.1(b) | Alter / Replace |  | Driving Machine Components - affected component complies w/ | Major
|  |  | 2.24.2 | Sheaves and Drums |  |  | mrr | Major
|  |  | 2.24.3 | Factor of Safety for Driving Machines and Sheaves
|  |  | 2.24.4 | Fasteners Transmitting Load
|  |  | 2.24.5 | Shafts Fillets and Keys
|  |  | 2.24.6 | Cast-Iron Worms and Worm Gears
|  |  | 2.24.7 | Friction Gearing and Clutches
|  |  | 2.24.8 | Braking Systems & Driving Machine Brakes |  |  | mrr | Major
|  |  | 2.24.9 | Indirect-Driving Machines
|  |  | 2.26.8 | Release and Application of Driving-Machine Brakes
| 8.7.2.25.1(c) | Change of |  | Driving Machine Sheave | Major | - | mrr | Major
|  |  | 2.24.2 | Sheaves and Drums
|  |  | 2.24.3 | Factor of Safety for Driving Machines and Sheaves
|  |  | 2.24.4 | Fasteners Transmitting Load
|  |  | 2.20. | Suspension Ropes & Connections
| 8.7.2.25.2 | Change in Location of Driving Machine |  |  | Major | -
| 8.7.2.25.2(a) | Change in Location of Driving Machine w/ no change in Rise |  |  | Major | -
|  |  | 2.7.2 | Maintenance Path and Clearance
|  |  | 2.9. | Machinery & Sheave Beams, Supports, Foundation
|  |  | 2.10.1 | Guarding of Equipment
|  |  | 2.24.2.3 | Traction
| 8.7.2.25.2(b) | Change in Location of Driving Machine w/ change in Rise |  |  | Major | -
|  |  | Part 2 (*) | Electric Elevators (entire installation to meet Part 2), except
2.5 Horizontal Car and Counterweight Clearances
2.11 Protection of Hoistway Openings
2.4 Vertical Clearances and Runbys for Cars & Cwts
|  |  | 8.7.2.5 | see also
|  |  | 8.7.2.10 | see also
| CAD 8.7.2.25«1 | « Replacement of worm and/or gear (specify make) |  |  | - | - | mrr | Minor A
|  |  | 2.24 | specify compliance to the applicable requirements
Addition of Machine Guarding - see CAD 8.7.2.7«1
| 8.7.2.26 | Terminal-Stopping Devices |  |  | Minor B | Minor B
|  |  | 2.25. | Terminal Stopping Devices
| 8.7.2.27 | Operating Devices and Control Equipment |  |  | ò See Below ò
| 8.7.2.27.1 | Top-of-Car Operating Devices |  |  | Minor A | Minor A | mrr | Minor A
|  |  | 2.26.1.4 | Inspection Operation
| CAD 8.7.2.27«1 | Alteration / Addition of any type of inspection operation |  |  | Minor A | Minor A
|  |  | 2.26.1.4 | Inspection Operation
| CAD 8.7.2.27«2 | « | Addition of Top-of-Car Operating Device (see CAD 3.8.3) |  | - | Minor A
|  |  | 2.26.1.4 | Inspection Operation
8.7.2.15«1,«2
| 8.7.2.27.2 | Car-Leveling or Truck-Zoning Devices |  |  | Minor A | Minor A
|  |  | 2.26.1.6 | Operation in Leveling or Truck Zone
| CAD 8.7.2.27«3 | « Door By-Pass Switches |  |  | Minor A | Minor A
|  |  | 2.26.1.5 | System to Prevent Auto Operation w/faulty Door Contacts
| CAD 8.7.2.27«4 | « Door Monitoring System |  |  | Minor A | Minor A
|  |  | 2.26.5 | System to Prevent Auto Operation w/faulty Door Contacts
| 8.7.2.27.3 | Change in Power Supply |  |  | Major | -
(a) voltage, frequency or # of phases or
(b) AC to DC , DC to AC or
(c) combination of DC & AC, then
electrical to:
|  |  | 2.26.1.1 | Types of Operation
|  |  | 2.26.1.2 | For Car-Switch Operation Elevators
|  |  | 2.26.1.3 | Add'l Operating Devices for Elevators carrying 1pc. load > than Rated
|  |  | 2.26.1.4 | Inspection Operation
|  |  | 2.26.1.6 | Operation in Leveling or Truck Zone
|  |  | 2.26.2 | Electrical Protective Devices
|  |  | 2.26.6 | Phase Protection of Motors
|  |  | 2.26.7 | Installation of Capacitors/Devices Making EPD's Ineffective
|  |  | 2.26.9 | Control & Operating Circuits
|  |  | 2.26.10 | Absorption of Regenerated Power
new / modified equipment and wiring to:
|  |  | 2.26.4.1 | Electrical Equipment and Wiring
|  |  | 2.26.4.2 | Drive Machine Controllers for Stopping/Starting/Controlling
|  |  | 2.26.4.3 | Positively Opened Contacts
brakes to:
|  |  | 2.24.8 | Braking Systems & Driving Machine Brakes
|  |  | 2.26.8 | Release and Application of Driving-Machine Brakes
winding drum to:
|  |  | 2.25.3.5 | Additional Req'mts for Winding Drum Machines
see 8.7.2.17.2(b) Increase in Rated Speed
| 8.7.2.27.4 | Controllers
| 8.7.2.27.4(a) | Install / Replace |  | Motion or Operation Controller (no change in method) | Major | - | Major
|  |  | 2.25. | Terminal Stopping Devices
|  |  | 2.26.1.4 | Inspection Operation
|  |  | 2.26.1.5 | Inspection Operation with Open Door Circuits
|  |  | 2.26.1.6 | Operation in Leveling or Truck Zone
|  |  | 2.26.2 | Electrical Protective Devices
|  |  | 2.26.3 | Contactor and Relays for Use in Critical Operating Circuits
|  |  | 2.26.4 | Electrical Equipment and Wiring
|  |  | 2.26.5 | System to Monitor & Prevent Automatic Operation w/ Faulty Door Contacts
|  |  | 2.26.6 | Phase Protection of Motors
|  |  | 2.26.7 | Installation of Capacitors/Devices Making EPD's Ineffective
|  |  | 2.26.8 | Release and Application of Driving-Machine Brakes
|  |  | 2.26.9 | Control & Operating Circuits
|  |  | 2.26.11 | Car Platform to Hoistway Door Sills Vertical Distance
levelling accuracy to 13mm (0.5 in.)
|  |  | 2.29. | Identification of Equipment and Floors
|  | « | 2.7.9.2 | Temperature and Humidity
|  |  | 2.27.2 | Emergency or Standby Power systems
If FEO previously present or required by OBC;
|  |  | 2.27.3 | Firefighters' Emergency Operation - Automatic Elevators
2.27.3.1 Phase 1 Recall Operation
2.27.3.2 Phase 1 Recall Operation by FAID's
CAD 2.27.3.2.2
2.27.3.3 Phase 2 Emergency In-Car Operation
2.27.3.4 Interruption of Power
2.27.3.5 Multicompartment Elevators
see 8.7.1.2 safety levels shall not be diminished
|  |  | 2.27.4 | FEO: Non Automatic Elevators
|  |  | 2.27.5 | FEO: Automatic Elevators with Designated-Attendant Operation
|  |  | 2.27.6 | FEO: Inspection Operation
|  |  | 2.27.7 | FEO: Operating Procedures
|  |  | 2.27.8 | Switch Keys
|  |  | 2.27.9 | Elevator Corridor Call Station Pictograph
If FEO NOT previously present or required by OBC;
CAD 2.27.3.2.2
2.27.3.1 Provide Phase 1 Manual Recall Operation Only
| CAD 8.7.2.27«5 | Relocation of |  | Elevator Controller (if control wiring disconnected - reconnected) | Major
|  |  | 2.8.2 | Electrical Equipment and Wiring
Electrical testing to verify functionality of rewired equipment
| 8.7.2.27.4(b) | Installation of |  | Door Controller | Minor A | - | Minor B
|  |  | 2.26.4.1 | Electrical Equipment and Wiring
|  |  | 2.26.4.2 | Drive Machine Controllers for Stopping/Starting/Controlling
| 8.7.2.27.4(c) | Installation of |  | Controller for Emergency or Standby Power | Minor A | Minor A | Minor B
|  |  | 2.26.4.1 | Electrical Equipment and Wiring
|  |  | 2.26.4.2 | Drive Machine Controllers for Stopping/Starting/Controlling
| 8.7.2.27.4(c) | Installation of |  | Controller for FEO Operation | Minor A | Minor A | Minor B
|  |  | 2.26.4.1 | Electrical Equipment and Wiring
|  |  | 2.26.4.2 | Drive Machine Controllers for Stopping/Starting/Controlling
| 8.7.2.27.5 | Change in Type of Motion Control - AC, VVVF, DC, SCR |  |  | Major | -
|  |  | 2.11.1(*) | Entrances and Emergency Doors Required
|  |  | 2.11.2 | Types of Entrances
|  |  | 2.11.3 | Closing of Hoistway Doors
|  |  | 2.11.4 | Location of Horizontally Sliding or Swinging H/W Doors
|  |  | 2.11.5 | Projection of Entrances & Equip. Beyond Land'g Sills
|  |  | 2.11.6(*) | Opening of Hoistway Doors
|  |  | 2.11.8 | Weights for Closing or Balancing Doors
|  |  | 2.11.9 | Hoistway Door Locking Devices & Power Operation
|  |  | 2.11.11.8(*) | Hoistway Door Safety Retainers
|  |  | 2.11.12.8 | Pull Straps
|  |  | 2.12.(*) | H/W-Door Locking Devices, Elec. Contacts, H/W Access
2.12.5 Restricted Opening of Hoistway or Car Doors
2.12.6 Hoistway Door Unlocking Devices
2.12.7 Hoistway Access Switches
|  |  | 2.13. | Power Operation of H/W Doors and Car Doors
|  |  | 2.14.(*) | Car: Enclosure, Doors, Gates, Illumination
2.14.1.7 car top railing
|  |  | 2.16.8(*) | Capacity & Loading
|  |  | 2.17.(*) | Car & Cwt Safeties
|  |  | 2.18.(*) | Speed Governors
|  |  | 2.19. | Ascending Car Overspeed & Unintended Car Movement Protection
|  |  | 8.7.2.20 | ACO & UCM Protection
|  | CAD | 8.7.2.20«1 | Pre B44-00 ACO & UCM Protection
|  | CAD | 8.7.2.20«2 | Pre B44-00 ACO Only Protection
|  | CAD | 8.7.2.20«3 | Addition ACO/UCM if not required by other alteration scope
|  |  | 2.25. | Terminal Stopping Devices
|  |  | 2.26.(*) | Operating Devices and Control Equipment
|  |  | 2.29. | Identification of Equipment and Floors
|  | « | 2.7.9.2 | Temperature and Humidity
If FEO previously present or required by OBC;
|  |  | 2.27. | Emergency Operation and Signalling Devices
2.27.1 Car Emergency Signalling Devices
2.27.2 Emergency or Standby Power Systems
2.27.3 Firefighters' Emergency Operation: Automatic Elevators
2.27.3.1 Phase 1 Recall Operation
2.27.3.2 Phase 1 Recall Operation by FAID's
CAD 2.27.3.2.2
2.27.3.3 Phase 2 Emergency In-Car Operation
2.27.3.4 Interruption of Power
2.27.3.5 Multicompartment Elevators
see 8.7.1.2 safety levels shall not be diminished
2.27.4 FEO: Non Automatic Elevators
2.27.5 FEO: Automatic Elevators with Designated-Attendant Operation
2.27.6 FEO: Inspection Operation
2.27.7 FEO: Operating Procedures
2.27.8 Switch Keys
If FEO NOT previously present or required by OBC;
CAD 2.27.3.2.2
2.27.3.1 Provide Phase 1 Manual Recall Operation Only
| 8.7.2.27.6 | Change in Type of Operation Control - CPPB, AUTOMATIC |  |  | Major | -
|  |  | 2.11.1 | Entrances and Emergency Doors Required
|  |  | 2.11.2 | Types of Entrances
|  |  | 2.11.3 | Closing of Hoistway Doors
|  |  | 2.11.4 | Location of Horizontally Sliding or Swinging H/W Doors
|  |  | 2.11.5 | Projection of Entrances & Equip. Beyond Land'g Sills
|  |  | 2.11.6 | Opening of Hoistway Doors
|  |  | 2.11.7 | Glass in Hoistway Doors
|  |  | 2.11.8 | Weights for Closing or Balancing Doors
|  |  | 2.11.9 | Hoistway Door Locking Devices & Power Operation
|  |  | 2.11.10 | Landing Sill: Guards, Illumination, hinged sills, Tracks
|  |  | 2.11.11 | Entrances, Horizontal Slide Type
|  |  | 2.11.12 | Entrances, Vertical Slide Type
|  |  | 2.11.13 | Entrances, Swing Type
|  |  | 2.12. | H/W-Door Locking Devices, Elec. Contacts, H/W Access
|  |  | 2.13. | Power Operation of H/W Doors and Car Doors
|  |  | 2.14.(*) | Car: Enclosure, Doors, Gates, Illumination
|  |  | 2.16. | Capacity & Loading
|  |  | 2.17. | Car & Cwt Safeties
|  |  | 2.18.(*) | Speed Governors
|  |  | 2.25. | Terminal Stopping Devices
|  |  | 2.26.(*) | Operating Devices and Control Equipment
|  |  | 2.29. | Identification of Equipment and Floors
|  | « | 2.7.9.2 | Temperature and Humidity
|  |  | 2.27. | Emergency Operation & Signaling Devices
2.27.1 Car Emergency Signalling Devices
2.27.2 Emergency or Standby Power Systems
2.27.3 FEO: Automatic Elevators
CAD 2.27.3.2.2
2.27.4 FEO: Non-Automatic Elevators
2.27.5 FEO: Automatic Elevators w/Attendant
2.27.6 FEO: Inspection Operation
2.27.7 FEO: Operating Procedures
2.27.8 Switch Keys
2.27.9 Elevator Corridor Call Station Pictograph if reqd by OBC
| CAD 8.7.2.27«6 | « Addition of Wander Patient Feature - Change in Operation Control |  |  | Minor B | Minor B
|  |  | 2.13.5.3 | - door time out
|  |  | 2.27.3.1.6(l) | - shall not prevent PHI
| CAD 8.7.2.27«7 | « Addition of Restricted Access - Security / Floor Lock Out |  |  | Minor B | Minor B
|  |  | OBC-3.2.6.5(4) | - shall not prevent floor access when on FEO
D.O. Button Remain Operative Under non FEO Conditions, Door Closed When not in Use
|  |  | 2.27.3.3.1(i) | - permit travel to all landings when on PH II
|  |  | 2.11.6.2 | Cannot Lock Out Top& Btm, Designated & Alternate or All Landings in Phase II
| CAD 8.7.2.27«8 | « Addition of Destination Dispatch |  |  |  | Minor B
|  |  | 8.7.2.8 | Electrical Equipment, Wiring, Pipes, and Ducts in H/W's &M/C Rooms
FEO operation to 8.7.2.28 or code at time of installation or alteration
| 8.7.2.27.7 | Removal of emergency stop switch on passenger elevators |  |  | Minor B | -
remove all related markings / engravings & provide an in-car stop switch to:
|  |  | 2.26.2.21 | In-car stop switch
|  | « | 2.26.4.3 | Positively Opened Contacts
|  | « | 2.26.9.3 | Single failure does not render In-Car Stop Sw ineffective
| 8.7.2.27.8 | Electrical Protective Devices |  |  | ò See Below ò
| 8.7.2.27.8 | Alteration or Addition of an Electrical Protective Device |  |  | Major | Major | mrr | Major
if device meets 2.26.4.3.2 (PES)
|  |  | 2.26.2 | Electrical Protective Devices - for specified device
| 8.7.2.27.8 | Alteration or Addition of an Electrical Protective Device |  |  | - | Minor A | mrr
if device meets 2.26.4.3.1
|  |  | 2.26.2 | Electrical Protective Devices - for specified device
| 8.7.2.28 | Emergency Operation and Signaling Devices |  |  | ò See Below ò
| 8.7.2.28 | Car Emergency Signaling Devices |  |  | Minor B | Minor B | mrr
|  |  | 2.27.1 | Car Emergency Signaling Devices
| 8.7.2.28 | Emergency or Standby Power |  |  | Minor B | Minor A
|  |  | 2.27.2 | Emergency Or Standby Power systems
| 8.7.2.28 | Firefighter's Emergency Operation |  |  | Minor B | Minor A
|  |  | 2.27.3 | FEO: Automatic Elevators
|  |  | 2.27.4 | FEO: Non-Automatic Elevators
|  |  | 2.27.5 | FEO: Automatic Elevators w/Attendant
|  |  | 2.27.6 | FEO: Inspection Operation
|  |  | 2.27.7 | FEO: Operating Procedures
|  |  | 2.27.8 | Switch Keys
| 8.7.2.28 | Addition of Elevator to a Group - all elevators to meet: |  |  | - | Minor A
|  |  | 2.27. | Emergency Operation & Signaling Devices
2.27.1 Car Emergency Signalling Devices
2.27.2 Emergency or Standby Power Systems
2.27.3 FEO: Automatic Elevators
CAD 2.27.3.2.2
2.27.4 FEO: Non-Automatic Elevators
2.27.5 FEO: Automatic Elevators w/Attendant
2.27.6 FEO: Inspection Operation
2.27.7 FEO: Operating Procedures
2.27.8 Switch Keys
2.27.9 Elevator Corridor Call Station Pictograph if reqd by OBC
| CAD 8.7.2.28«1 | « Emerg. Recall Upgrade - from Manual to Automatic & matching code at time of install |  |  | Minor B
conformance to auto recall based on F.S. at time of install
| CAD 8.7.2.28«2 | « Emerg. Recall Upgrade to comply with a Fire Code Retrofit Order |  |  | Minor B | Minor A
2.27.3 FEO: Automatic Elevators
|  |  | CAD 3.20 | Fire Code Retrofits
| 8.7.3.« | Alteration - Hydraulic to Electric Elevator
| 8.7.3.«1 | Where a hydraulic elevator operated in an existing hoistway and a new electric elevator will be installed in its place, the following conditions will apply: |  |  | New
|  | « | Part 2 | Electric Elevators, except:
|  | « |  | Existing building conditions not in full conformance with current requirements may be retained. Identify each deviation in the submission (box 4000) ie.
- pit depth
- no pit drain
|  | « |  | A New Installation Number will be issued
|  | « | 2.15.9 | Apron plate length per 2.15.9 or
- collapsible / telescopic / folding design utilized
| 8.7.3 | Alterations to Hydraulic Elevators
| 8.7.3.1 | Hoistway Enclosures |  |  | see 8.7.2.1
| 8.7.2.1 | Hoistway Enclosures |  |  | Major | Major
| 8.7.2.1.1 | Hoistway Enclosure Walls |  |  | Major | Major
|  |  | 2.1.1 | Hoistway Enclosures
|  |  | 2.1.5 | Windows and Skylights
|  |  | 2.1.6 | Projections, Recesses, and Setbacks in H/W
|  |  | 2.5. | Horizontal Car and Counterweight Clearances
|  |  | 2.7.3.4.6 | Access Doors and Openings
|  | « | 2.7.3.4.7 | Access Doors and Openings
|  |  | 2.8. | Equipment in Hoistways,Machinery Spaces, Machine Rooms, Control Spaces, and Control Rooms
|  |  | 8.7.2.10 | Entrances and Hoistway Openings (if change includes an entrance)
|  |  | 2.11.1 | Entrances and Emergency Doors Required (if blind H/W)
| 8.7.2.1.2 | Addition of Elevator to Existing Hoistway |  |  | - | New
|  |  | B44-2010 | New Installation
|  |  | 2.5. | Horizontal Car and Counterweight Clearances
| 8.7.2.1.3 | Construction at Top of Hoistway |  |  | Major | Major
|  |  | 2.1.2.1 | Construction at Top of the Hoistway
|  |  | 2.1.3 | Floor Over Hoistways
|  |  | 8.7.2.4 | Vertical Car & Cwt Clearances & Runbys
| 8.7.2.1.4 | Construction at Bottom of Hoistway |  |  | Major | Major
|  |  | 2.1.2.2 | Construction at Bottom of the Hoistway
|  |  | 2.1.2.3 | Strength of Pit Floor
|  |  | 2.2. | Pits
|  |  | 8.7.2.4 | Vertical Car & Cwt Clearances & Runbys
| 8.7.2.1.5 | Control of Smoke and Hot Gases |  |  | Major | Major
|  |  | 2.1.4 | Control of Smoke and Hot Gases
| 8.7.3.2 | Pits |  |  | see Electric Elevators
| 8.7.2.2 | Pits | see other alterations below for non Major Alterations |  | Major | -
|  |  | 2.2. | Pits
|  |  | 2.1.2.3 | Strength of Pit Floor
|  |  | 8.7.3.4 | Vertical Car & Cwt Clearances & Runbys
| 8.7.2.2 | Pit Drains & Sumps |  |  | Minor B | Minor B
|  |  | 2.2.2. | Pit Drains
| 8.7.2.2 | Pit Guards |  |  | Minor B | Minor A
|  |  | 2.2.3 | Guards Between Adjacent Pits
| 8.7.2.2 | Pit Access |  |  | Minor B | Minor A
|  |  | 2.2.4 | Pit Access
| 8.7.2.2 | Pit Illumination |  |  | Minor B | Minor B
|  |  | 2.2.5 | Illumination of Pits
| 8.7.2.2 | Pit Stop Switches |  |  | Minor B | Minor A
|  |  | 2.2.6 | Stop Switches
| 8.7.2.2 | Pit Depth |  |  | Minor B | Minor A
|  |  | 2.2.7 | Minimum Pit Depths Required
| 8.7.2.2 | Access to Underside of Car |  |  | Minor B | Minor A
|  |  | 2.2.8 | Access to Underside of Car
| 8.7.3.3 | Location and Guarding of Counterweights |  |  | Major | Major
|  |  | 2.3. | Location and Guarding of Counterweights
|  |  | 2.5.1.2 | Between Car & Cwt and Cwt Guard
|  |  | 3.5. | Horizontal car and Counterweight Clearances
| 8.7.3.4 | Vertical Car and Counterweight Clearances and Runbys (no reduction allowed) |  |  | Major | -
|  |  | 3.4. | Bottom and Top Clearances and Runbys for Cars and Cwts
|  |  | 8.7.3.22.1 | Increase or Decrease in Rise
|  |  | 8.7.3.22.2 | Increase in Rated Speed
|  |  | 8.7.3.23.5 | Change in Location of Hydraulic Jack
| 8.7.3.5 | Horizontal Car and Counterweight Clearances (no reduction allowed) |  |  | Major | -
|  |  | 2.5. | Horizontal Car and Counterweight Clearances
|  |  | 8.7.3.22.1 | Increase or Decrease in Rise
|  |  | 8.7.3.22.2 | Increase in Rated Speed
|  |  | 8.7.3.23.5 | Change in Location of Hydraulic Jack
| 8.7.3.6 | Protection of Spaces Below Hoistways |  |  | Minor B | Major
|  |  | 3.6. | Protection of Spaces below Hoistway
| 8.7.3.7 | Machine Rooms and Machinery Spaces |  |  | see 8.7.2.7
| 8.7.2.7 | Machine Rooms and Machinery Spaces |  |  | ò See Below ò
| 8.7.2.7.1 | Enclosures - other than specifics of 8.7.2.7.2 to 8.7.2.7.7
|  |  | 2.7. (& 3.7.) | New - Machinery Spaces, Machine Rooms Control Spaces & Control Rooms | - | Major
|  |  | 2.7. (& 3.7.) | Altered- Machinery Spaces, Machine Rooms Control Spaces & Control Rooms | Minor A | -
|  |  | OESC (C22.1) | Electrical Equipment Clearances | Minor B | -
| 8.7.2.7.2 | Means of Access |  |  | Minor B | -
|  |  | 2.7.3.1 | General Requirements
|  |  | 2.7.3.2 | Access Across Roofs
|  |  | 2.7.3.3 | Means of Access
| 8.7.2.7.3 | Access Doors and Openings |  |  | Minor B | Minor B | mrr
|  |  | 2.7.3.4 | Access Doors and Openings
|  |  | 2.7.3.5 | Stop Switch in O/H M/C Space in the H/W
| 8.7.2.7.4 | Headroom (no reduction) |  |  | Minor B | Minor B
|  |  | 2.7.4 | Headroom in M/C Rooms
| 8.7.2.7.5 | Windows and Skylights |  |  | Minor B | Minor B
2.1.5
| 8.7.2.7.6 | Lighting (no reduction) |  |  | Minor B | Minor A
|  |  | 2.7.9.1 | Lighting
| 8.7.2.7.7 | Ventilation |  |  | Minor B | Minor B
|  |  | 2.7.9.2 | Temperature & Humidity
| CAD 8.7.2.7«1 | Addition of Elevator Equipment Guarding |  |  | Minor A (per m/c rm) |  | mrr | mrr
|  |  | 2.7.2 | Maintenance Path and Clearance
|  |  | 2.7.3.4.2 | Size of doors and openings in cage style enclosures (750x2030)
|  |  | 2.10.1 | Guarding of Equipment
openable/removable only with tools
operating/work instruction for accessing equipment
clearances in front of electrical control equipment (1000mm)
access in front of / space to operate main disconnect (750mm)
Installation by registered contractor
| 8.7.3.8 | Electrical Wiring, Pipes, and Ducts in Hoistways and Machine Rooms |  |  | Minor B | Minor B | mrr | Minor B
|  | Installation of New (electrical equipment, wiring, raceways, cables, pipes, ducts) |  |  | - | Minor B
also installation of Monitoring Equipment, HVAC
|  |  | 2.8. | Equipment in Hoistways and Machine Rooms
CSA Labeling (or equivalent)
OESC, CSA C22.1 as required
|  | Alteration of Existing (electrical equipment, wiring, raceways, cables, pipes, ducts…) |  |  | Minor B | -
|  |  | 2.8. | Equipment in Hoistways and Machine Rooms
| 8.7.3.9 | Machinery and Sheave Beams, Supports and Foundations |  |  | Major | Major
New/Relocated Machinery & Sheave Beams, Supports, Foundation
|  |  | 2.9. | Machinery & Sheave Beams, Supports, Foundation
Building reactions increased by more than 5%
|  |  | 2.9. | Machinery & Sheave Beams, Supports, Foundation
adequacy of building structure verified by P.Eng.
| 8.7.3.10 | Hoistway Entrances and Openings - see 8.7.2.10 |  |  | see 8.7.2.10
| 8.7.2.10 | Entrances and Hoistway Openings |  |  | Major | Major | see below
| 8.7.2.10.1 | General Requirements |  |  | Major | -
| 8.7.2.10.1(a) | General Requirements - All New Entrances |  |  | Major | -
|  |  | 2.11. | Protection of H/W Openings
|  |  | 2.12. | H/W-Door Locking Devices, Elec. Contacts, H/W Access
|  |  | 2.13. | Power Operation of H/W Doors and Car Doors
|  |  | 2.29.2 | Identification of Floors
| 8.7.2.10.1(b) | General Requirements - New Entrances w/Existing Entrances |  |  | - | Major
|  |  | 2.11.2 | Types of Entrances
|  |  | 2.11.3 | Closing of Hoistway Doors
|  |  | 2.11.4 | Location of Horizontally Sliding or Swinging H/W Doors
|  |  | 2.11.5 | Projection of Entrances & Equip. Beyond Land'g Sills
|  |  | 2.11.6 | Opening of Hoistway Doors
|  |  | 2.11.7 | Glass in Hoistway Doors
|  |  | 2.11.8 | Weights for Closing or Balancing Doors
|  |  | 8.7.2.10.5 | Marking of Entrance Assemblies
Entire installation to meet:
|  |  | 2.11.6 | Opening of Hoistway Doors
|  |  | 2.12. | H/W-Door Locking Devices, Elec. Contacts, H/W Access
|  |  | 2.13. | Power Operation of H/W Doors and Car Doors
|  |  | 2.29.2 | Identification of Floors
| 8.7.2.10.1(c) | General Requirements - Alteration to H/W Entrance |  |  | Major | -
|  |  | 2.11.3 | Closing of Hoistway Doors
|  |  | 2.11.5 | Projection of Entrances & Equip. Beyond Land'g Sills
|  |  | 2.11.7 | Glass in Hoistway Doors
|  |  | 2.11.8 | Weights for Closing or Balancing Doors
|  |  | 8.7.2.10.5 | Marking of Entrance Assemblies
Entire installation to meet:
|  |  | 2.12. | H/W-Door Locking Devices, Elec. Contacts, H/W Access
|  |  | 2.13. | Power Operation of H/W Doors and Car Doors
|  |  | 2.29.2 | Identification of Floors
| 8.7.2.10.1(d) | General Requirements - Emergency Doors (added or altered) |  |  | Major | Major
|  |  | 2.11.1 | Entrances and Emergency Doors Required
|  |  | 8.7.2.10.5 | Marking of Entrance Assemblies
| 8.7.2.10.1(e) | General Requirements - Access Openings (installed for cleaning) |  |  | Major | Major
|  |  | 2.11.1.4 | Access Opening for Cleaning of Car & H/W Enclosure
|  |  | 8.7.2.10.5 | Marking of Entrance Assemblies
| 8.7.2.10.2 | Horizontal Slide-Type Entrances - new entrance and components to meet: |  |  | Major | Major | see below
|  |  | 8.7.2.10.1 | Entrances & H/W Openings - General Req'mts |  |  | Major
|  |  | 2.11.11 | Entrances, Horizontal Slide Type
| sills (a) |  | 2.11.10.1 | Landing-Sill Guards | Minor B |  | Minor B
|  |  | 2.11.11.1 | Landing Sills
|  |  | 2.11.11.6 | Bottom Guides
| track (b) |  | 2.11.11.2 | Hanger Tracks, and Track Supports | Minor B |  | Minor B
| frame (c) |  | 2.11.11.3 | Entrance Frames | Minor A |  | Minor A
|  |  | 2.11.11.5.1 | Panel Overlap
|  |  | 2.11.11.5.2 | Panel Gaps Clearances
|  |  | 2.11.11.5.3 | Pockets in Strike Jamb
|  |  | 8.7.2.10.5 | Marking of Entrance Assemblies
| hangers (d) |  | 2.11.11.4 | Hangers | Minor B |  | Minor B
| panels (e) |  | 2.11.11.5(*) | Panels | Minor A |  | Minor A
|  |  | 2.11.11.6 | Bottom Guides
|  |  | 2.11.11.7 | Multipanel Entrances
|  |  | 8.7.2.10.5 | Marking of Entrance Assemblies
| retainers (f) |  | 2.11.11.8 | Hoistway Door Safety Retainers | Minor B |  | Minor B
| 8.7.2.10.3 | Vertical-Slide-Type Entrances - new entrance and components to meet: |  |  | Major | Major | see below
|  |  | 8.7.2.10.1 | Entrances & H/W Openings - General Req'mts |  |  | Major
|  |  | 2.11.12 | Entrances, Vertical Slide Type
| sills (a) |  | 2.11.10.3 | Hinged Hoistway Landing Sills | Minor B |  | Minor B
|  |  | 2.11.12.1 | Landing Sills
| frames (b) |  | 2.11.12.2 | Entrances Frames | Minor B |  | Minor B
|  |  | 8.7.2.10.5 | Marking of Entrance Assemblies
| rails (c) |  | 2.11.12.3 | Rails | mrr |  | mrr
| panels (d) |  | 2.11.12.4 | Panels | Minor A |  | Minor A
|  |  | 2.11.12.3 | Rails
|  |  | 2.11.12.5 | Guides
|  |  | 2.11.12.6 | Counterweighting or Counterbalancing
|  |  | 2.11.12.8 | Pull Straps
|  |  | 8.7.2.10.5 | Marking of Entrance Assemblies
| guides (e) |  | 2.11.12.5 | Guides | mrr |  | mrr
| sill guard (f) |  | 2.11.12.7 | Sill Guards
| straps (g) |  | 2.11.12.8 | Pull Straps
| 8.7.2.10.4 | Swing-Type Entrances - new entrance and components to meet: |  |  | Major | Major | see below
|  |  | 8.7.2.10.1 | Entrances & H/W Openings - General Req'mts |  |  | Major
|  |  | 2.11.13 | Entrances, Swing Type
| sills (a) |  | 2.11.10.1 | Landing-Sill Guards | Minor B |  | Minor B
|  |  | 2.11.10.3 | Hinged Hoistway Landing Sills
|  |  | 2.11.13.1 | Landing Sills
| frames (b) |  | 2.11.13.2 | Entrance Frames | Minor B |  | Minor B
|  |  | 2.11.13.4 | Hinges
|  |  | 8.7.2.10.5 | Marking of Entrance Assemblies
| panels (c) |  | 2.11.13.3 | Panels | Minor B |  | Minor B
|  |  | 2.11.13.4 | Hinges
|  |  | 2.11.13.5 | Marking
|  |  | 8.7.2.10.5 | Marking of Entrance Assemblies
| hinges (d) |  | 2.11.13.4 | Hinges | mrr |  | mrr
| 8.7.2.10.5 | Marking of Entrance Assemblies (Alteration to an Entrance Door Panel) |  |  | Major | Major
Fire Protection Rating not less then existing entrance
|  |  | 8.7.2.10.5(a) | NBCC requirements
| CAD 8.7.2.10«1 | « Removing Service To a Floor |  |  | Minor B
Bolt entrances shut
Remove Interlock From Safety String
Remove COP Floor Button
|  |  | 2.11.6.2 | Cannot Lock Out Top/Btm, Designated/Alternate, All Landing in Phase II
|  |  | 2.12.7 | H/W Access Switches - if floor was previously the access location
| CAD 8.7.2.10«2 | « Door Safety Retainers |  |  | Minor B | Minor A | mrr | Minor B
|  |  | 2.11.11.8 | Hoistway Door Safety Retainers
| 8.7.3.11 | Hoistway Door-Locking Devices |  |  | See 8.7.2.11
| 8.7.2.11 | Hoistway Door-Locking Devices, Access Switches & Parking Devices |  |  | ò See Below ò
| 8.7.2.11.1 | Interlocks |  |  | - | Major | mrr | Minor B
|  |  | 2.12.1 | General
|  |  | 2.12.2 | Interlocks
|  |  | 2.12.4 | Listing/Certification Locking Devices
|  |  | 2.12.5 | Restricted Opening of H/W or Car Door (n/a for column 5,6) |  |  | n/a
|  |  | 2.12.6 | Hoistway Door Unlocking Devices (n/a for column 5,6) |  |  | n/a
|  |  | 2.12.7 | Hoistway Access Switches (n/a for column 5,6) |  |  | n/a
| 8.7.2.11.2 | Mechanical Locks and Electric Contacts |  |  | - | Major | mrr | Minor B
|  |  | 2.12.1 | General
|  |  | 2.12.3 | H/W Door Combination Mechanical Locks & Contacts
|  |  | 2.12.4 | Listing/Certification Locking Devices
|  |  | 2.12.6 | Hoistway Door Unlocking Devices
| 8.7.2.11.3 | Parking Devices |  |  | Minor A | Minor A
|  |  | 8.7.2.11.3 | requirements specified
| 8.7.2.11.4 | Access switches and Unlocking Devices
| 8.7.2.11.4 (a) | Addition of Unlocking Devices |  |  | - | Minor B | mrr
|  |  | 2.12.6 | Hoistway Door Unlocking Devices
| 8.7.2.11.4 (b) | Addition of Access Switches |  |  | - | Minor A | mrr
|  |  | 2.12.7 | Hoistway Access Switches
|  |  | 2.24.8 | Braking Systems & Driving Machine Brakes
|  |  | 2.26.1.4 | Inspection Operation
| 8.7.2.11.5 | Restricted Opening of H/W or Car Doors of Passenger Elevators (Restrictors) (Altered or Installed) |  |  | Minor B | Minor B | mrr | Minor B
|  |  | 2.12.5 | Restricted Opening of H/W or Car Door
| 8.7.3.12 | Power Operation of Hoistway Doors (Addition / Alteration to Power Open or Close) |  |  | Minor A | Minor A
|  |  | 8.7.2.10.1 | Entrances & H/W Openings - General Req'mts
|  |  | 8.7.2.10.2 | Horizontal Slide-Type Entrances
|  |  | 8.7.2.10.3 | Vertical Slide-Type Entrances
|  |  | 8.7.2.10.5 | Marking of Entrance Assemblies
|  |  | 8.7.3.10 | Hoistway Entrances and Openings
|  | « | 2.13. | Power Operation of Hoistway Doors and Car Doors
| CAD 8.7.2.12«1 | « Replacement of Door Operator |  |  | - | - | mrr | Minor B
|  |  | 2.13. | Power Operation of Hoistway Doors and Car Doors
8.7.2.15«1,«2
| CAD 8.7.2.12«2 | « Replacement of Door Reopening Device |  |  | See 8.7.2.13
| 8.7.2.13 | Door Reopening Device (Safety Edge) (Altered or Added or Replaced) |  |  | Minor B | Minor B | mrr | Minor B
|  |  | 2.13.4 | Closing Limitations for Power Operated HS Doors & Gates |  |  | see
|  |  | 2.13.5 | Reopening Device for Power Operated Car Doors or Gates |  |  | 8.6.3.8
if FEO provided, door opening & closing to PHI &II at time of install
8.7.2.15«1,«2
| 8.7.3.13 | Car Enclosures |  |  | See 8.7.2.14
| 8.7.2.14 | Car Enclosures, Car Doors and Gates, and Car Illumination |  |  | ò See Below ò
| 8.7.2.14.1 | Installation of New Car Enclosure |  |  | Major | -
|  |  | 2.14. | Car: Enclosure, Doors, Gates, Illumination
|  |  | 2.15. | Car Frames & Platforms
|  |  | 2.17 | Car and counterweight safeties
|  |  | 8.7.2.15.1 | Alterations to Car Frames and Platforms
| 8.7.2.14.2 | Alteration to Existing Cars |  |  | Minor A | Minor A
| 8.7.2.14.2(a) | Car Enclosure - Securing of Enclosures |  |  | Minor A | Minor A
|  |  | 2.14.1.2 | Securing of Enclosures
| 8.7.2.14.2(b) | Top Emergency Exit (Altered or Added) |  |  | Minor B | Minor B
|  |  | 2.14.1.5 | Top Emergency Exits
| 8.7.2.14.2(c) | Installation of Glass |  |  | Minor B | Minor B
|  |  | 2.14.1.8 | Glass in Elevator Cars
|  |  | 2.14.1.8.1 | Enclosures include glass
|  |  | 2.14.1.8.2 | Lining of Walls or Ceilings include glass |  |  | mrr
|  |  | 2.14.1.8.3 | Marking of each Glazing Panel
| 8.7.2.14.2(d) | Specific Equipment in Elevator Car |  |  | Minor B | Minor B
|  |  | 2.14.1.9 | Equipment Inside Cars
|  |  | (a) | Handrails
|  |  | (b) | fastening devices for protective linings
|  |  | (c) | ceiling mounted hooks/tracks
|  |  | (d) | picture frames display boards, plaques <38mm protrusion
secured to 2.14.1.2
material to 2.14.2.1
|  |  | (e) | conveyor tracks in freights
|  |  | ( f) | heating or cooling equipment
8.7.2.15«1,«2
| CAD 8.7.2.14«1 | « Car operating station |  |  | Minor B | Minor B | mrr | Minor B
verify inspection operation 'if provided'
verify stop sw
verify switches operate as before (eg. FS, FEO, Access)
8.7.2.15«1,«2
| CAD 8.7.2.14«2 | « video cameras / surveillance equipment / video monitors |  |  | Minor B | Minor B
|  |  | 2.8.2.1 | electrical equipment & wiring
|  |  | 2.14.1.2.3 | securing of enclosure equipment
|  |  | 2.14.2.4 | Headroom in Elevator Cars
8.7.2.15«1,«2
| CAD 8.7.2.14«3 | « other equipment |  |  | Variance
| 8.7.2.14.2(e) | Side Emergency Exits - Secured Shut |  |  | Major | -
| 8.7.2.14.2(f) | Car Ventilation |  |  | Minor B | -
|  |  | 2.14.2.3 | Ventilation
| 8.7.2.14.2(g) | Car Illumination |  |  | Minor B | Minor B
|  |  | 2.14.7 | Illumination of Cars and Lighting Fixtures
| 8.7.2.14.2(h) | Partitions Installed in Elevator Cars |  |  | Major | Major
|  |  | 2.16.1.2 | Use of Partitions for Reducing Inside Net Platform Area
| 8.7.2.14.2(i) | Installation of Car Door or Gate, Installation to meet: |  |  | Major | Major
|  |  | 2.14.4 | Passenger and Freight Car Doors/Gates, General Requirements
|  |  | 2.14.5 | Passenger Car Doors
|  |  | 2.14.6 | Freight Elevator Car Doors and Gates
| 8.7.2.14.4 | Car Enclosure / Car Door or Car Gates |  |  | ò See Below ò
| 8.7.2.14.4 | Alteration to Car Enclosure other than 8.7.2.14.2 - Enclosure Materials
|  |  | 2.14. | Car: Enclosure, Doors, Gates, Illumination
enclosure material flame ratings shall not be diminished
|  |  |  | 2.14.1.7 car top railing - see CAD 8.7.2.14«4 |  | Minor A
|  |  |  | 2.14.7.1.3 auxiliary lighting |  | Minor B
|  |  |  | 2.14.7.1.4 car top light & outlet |  | Minor B
|  |  | « | CAD 8.7.2.15«1 | Minor B |  | Minor B
or
|  |  | « | CAD 8.7.2.15«2 | Minor A |  | Minor A
| 8.7.2.14.4 | Alteration to Car Door or Car Gates other than 8.7.2.14.2 |  |  | Minor A | Minor A
|  |  | 2.14. | Car: Enclosure, Doors, Gates, Illumination
2.14.1.7 car top railing
2.14.7.1.3 auxiliary lighting
2.14.7.1.4 car top light & outlet
| O.Reg.209/01s30 | « Relocation of Elevator License to remote location |  |  | Minor B† | -
| CAD 8.7.2.14«4 | « Car Top Guard Rail |  |  | Minor B | Minor A | - | Minor A
|  | CAD | 8.7.2.14«4(a) | Standard Guardrail (to CAD 8.7.2.14«4(a), 2.14.1.7 & OBC)
or
|  | CAD | 8.7.2.14«4(b) | Foldable Guardrail (to CAD 8.7.2.14«4(b), 2.14.1.7 & OBC)
car top run buttons not enabled until extended
normal operation not enabled until stowed
electrical limits to ensure car top clearance in overhead
minor A submission template
|  |  | 8.7.2.15«1,«2 | car weighed prior to alteration
| 8.7.3.14 | Car Frames and Platforms |  |  | Major | - | Major
|  |  | 3.15. | Car Frames & Platforms
| 8.7.3.15 | Safeties |  | Car or Cwt (plunger gripper see 8.7.3.23.7) | ò See Below ò
| 8.7.3.15.1 | Car Safeties |  |  | - | Major | mrr | Minor A
|  |  | 3.17.1 | Car Safeties
|  |  | 3.23. | Guide Rails, Guide-Rail Supports, and Fastenings
|  |  | 3.28. | Layout Data
| 8.7.3.15.2 | Counterweight Safeties |  |  | - | Major | mrr | Minor A
|  |  | 3.17.2 | Counterweight Safeties
|  |  | 3.23. | Guide Rails, Guide-Rail Supports, and Fastenings
|  |  | 3.28. | Layout Data
| 8.7.3.15.3 | Alteration to existing Car or Counterweight Safeties |  |  | Major | - | mrr | Minor A
|  |  | 3.17(*) | Car and counterweight safeties and plunger gripper
|  |  | 3.23. | Guide Rails, Guide-Rail Supports, and Fastenings
|  |  | 3.28. | Layout Data
| 8.7.3.16 | Governors and Governor Ropes |  |  | See 8.7.2.19
| 8.7.2.19 | Speed Governors and Governor Ropes |  |  | Major | Major | òSee Below ò
| 8.7.2.19 |  | 2.18. | Speed Governors |  |  | mrr | Minor A
see
8.6.3.6
| 8.7.2.19 |  | 2.17.15 | Governor Rope Releasing Carriers |  |  | mrr | mrr
see 8.6.3.9
| 8.7.2.19 |  | Governor Ropes of different material or Construction to: |  |  |  | Minor B | Minor B
2.18.6 Design of Gov'r Rope Retarding Means for Type B Safeties
2.18.7 Traction between Speed Governor Rope & Sheave
|  |  | & testing to | 2.17.3 Function and Stopping Distances of Safeties
| 8.7.3.17 | Change in Type of Service: Passenger to Freight OR Freight to Passenger |  |  | Major | -
|  |  | 2.11.1(*) | Entrances and Emergency Doors Required
|  |  | 2.11.2 | Types of Entrances
|  |  | 2.11.3 | Closing of Hoistway Doors
|  |  | 2.11.5 | Projection of Entrances & Equip. Beyond Land'g Sills
|  |  | 2.11.6 | Opening of Hoistway Doors
|  |  | 2.11.7 | Glass in Hoistway Doors
|  |  | 2.11.8 | Weights for Closing or Balancing Doors
|  |  | 2.12. | H/W-Door Locking Devices, Elec. Contacts, H/W Access
|  |  | 2.13. | Power Operation of H/W Doors and Car Doors
|  |  | 2.22.(*) | Buffers & Bumpers
|  |  | 3.22.2 | Counterweight Buffers
|  |  | 3.14. | Car: Enclosure, Doors, Gates, Illumination
|  |  | 2.14. | Car: Enclosure, Doors, Gates, Illumination
|  |  | 2.14.1.7.1 | car top guard rail to 8.7.2.144
|  |  | 3.15. | Car Frames & Platforms
|  |  | 3.17. | Car and Counterweight Safeties
|  |  | 3.21. | Counterweights
|  |  | 3.23. | Guide Rails, Guide-Rail Supports, and Fastenings
|  |  | 2.18.(*) | Speed Governors
|  |  | 3.16. | Capacity & Loading
|  |  | 3.18. | Hydraulic Jacks
|  |  | 3.19. | Valves, Pressure Piping, and Fittings
|  |  | 3.20. | Ropes and Rope Connections
|  |  | 3.24. | Hydraulic Machines and Tanks
|  |  | 3.25. | Terminal-Stopping Devices
|  |  | 3.26. | Operating Devices and Control Equipment
|  |  | 3.27. | Emergency Operation and Signaling Devices
3.27.1 PHI Emergency Recall Operation After Device Actuation
(a) low oil protection
(b) plunger follower guide protection
(c) auxiliary power lowering
(d) oil tank temperature shutdown
2.27 Emergency Operation & Signaling Devices
2.27.1 Car Emergency Signalling Devices
2.27.2 Emergency or Standby Power Systems
2.27.3 FEO: Automatic Elevators
CAD 2.27.3.2.2
2.27.4 FEO: Non-Automatic Elevators
2.27.5 FEO: Automatic Elevators w/Attendant
2.27.6 FEO: Inspection Operation
2.27.7 FEO: Operating Procedures
2.27.8 Switch Keys
2.27.9 Elevator Corridor Call Station Pictograph if reqd by OBC
| 8.7.3.18 | Change in Class of Loading: [A, B, C1, C2, C3] |  |  | Major | -
|  |  | 2.16.2 | Minimum Rated Load for Freight Elevators
|  |  | 3.16. | Capacity & Loading
| 8.7.3.19 | Carrying of Passengers on Freight Elevators |  |  | Major | -
|  |  | 3.16.4 | 2.16.4 except 2.16.4.3
|  |  | 2.16.4 | Carrying of Passengers on Freight Elevators
|  |  | 2.16.4.1 | not accessible to general public
|  |  | 2.16.4.2 | rated load not less than required by 2.16.1
|  |  | 2.16.4.4 | H/W entrances to 2.12.1.1 & 2.11.2.1 or 2.11.2.2(e)
|  |  | 2.16.4.5 | car doors to 2.14.5 Passenger Car Doors
|  |  | 2.16.4.6 | car enclosure openings to 2.14.2.2 Prohibited Openings
|  |  | 2.16.4.7 | conforms to 2.12.5 Restricted Opening of H/W or Car Door
|  |  | 2.16.4.8 | Fs for suspension ropes to Table 2.20.3
|  |  | 2.16.4.9 | Power Operated vertical doors to 2.16.4.9(a) to (e)
|  |  | « | apron guard to ED CAD or extent pit permits
|  |  | « | 2.16.5 Signs Required in Freight Elevator Cars
| 8.7.3.20 | Increase in Rated Load |  |  | Major | -
|  |  | 2.26.1.4 | Inspection Operation
|  |  | 2.26.1.5 | Inspection Operation with Open Door Circuits
|  |  | 2.26.5 | Monitor & Prevent Automatic Operation w/ Faulty Door Contacts
|  |  | 3.14. | Car: Enclosure, Doors, Gates, Illumination
|  |  | 2.14. | Car: Enclosure, Doors, Gates, Illumination
|  |  | 2.14.1.7.1 | car top guard rail to CAD 8.7.2.144
|  |  | 3.15. | Car Frames & Platforms - «apron guard to ED CAD/as pit permits
|  |  | 3.16. | Capacity & Loading
|  |  | 3.17. | Car and Counterweight Safeties
|  |  | 3.20. | Ropes and Rope Connections
|  |  | 3.21. | Counterweights
|  |  | 3.22. | Buffers and Bumpers
|  |  | 3.23. | Guide Rails, Guide-Rail Supports, and Fastenings
|  |  | 8.7.3.23.4 | Increase in Working Pressure
| 8.7.3.21 | Increase in Deadweight of Car (Car Wt+Rated Load >5%) |  |  | Major | -
|  |  | 3.14. | Car: Enclosure, Doors, Gates, Illumination | n/a
|  |  | 2.14. | Car: Enclosure, Doors, Gates, Illumination
|  |  | 2.14.1.7.1 | car top guard rail to 8.7.2.144
|  |  | 3.15. | Car Frames & Platforms - «apron guard to ED CAD/as pit permits
|  |  | 3.16. | Capacity & Loading
|  |  | 3.17. | Car and Counterweight Safeties
|  |  | 3.20. | Ropes and Rope Connections
|  |  | 3.21. | Counterweights
|  |  | 3.22. | Buffers and Bumpers
|  |  | 3.23. | Guide Rails, Guide-Rail Supports, and Fastenings
|  |  | 3.24.5 | Counterweight Sheaves
|  |  | 8.7.3.23.4 | Increase in Working Pressure
CAD 8.7.2.15«1
| CAD 8.7.3.21«1 | « Decrease Deadweight <5% or Increase Deadweight of Car (115 kg or Less) |  |  | Minor B | Minor B
|  | CAD | 8.7.2.15«1
| CAD 8.7.3.21«2 | « Increase Deadweight of Car (>115 kg to 5%) |  |  | Minor A | Minor A
|  | CAD | 8.7.2.15«2
| 8.7.3.22 | Change in Rise or Rated Speed |  |  | Major | -
| 8.7.3.22.1 | Increase or Decrease in Rise |  |  | Major | -
|  |  | 3.25. | Terminal-Stopping Devices
|  |  | 3.4. | Bottom and Top Clearances and Runbys for Cars and Cwts
|  |  | 3.4.1 | Bottom Car Clearance
|  |  | 3.4.2 | Minimum Bottom and Top Car Runby
|  |  | 3.4.3 | Car Top and Bottom Maximum Runby
|  |  | 3.18.2 | Plungers
If decrease in rise is at lowest end then;
|  |  | 2.2.4 | Access to Pits
|  |  | 2.2.5 | Illumination of Pits
|  |  | 2.2.6 | Stop Switches
| 8.7.3.22.2 | Increase in Rated Speed |  |  | Major | -
|  |  | 2.5. | Horizontal Car and Counterweight Clearances
|  |  | 3.4. | Bottom and Top Clearances and Runbys for Cars and Cwts
|  |  | 3.21. | Counterweights
|  |  | 3.22.2(*) | Counterweight Buffers
|  |  | 3.14. | Car: Enclosure, Doors, Gates, Illumination
|  |  | 2.14. | New doors/gates to: Car: Enclosure, Doors, Gates, Illumination
|  |  | 3.17.(*) | Car and Counterweight Safeties
|  |  | 3.16. | Capacity & Loading
|  |  | 3.25. | Terminal-Stopping Devices
|  |  | 3.26.1 | Operating Devices and Control Equipment
|  |  | 3.26.2 | Inspection Operation
|  |  | 3.26.3 | Anti-Creep and Leveling Operation
|  |  | 3.26.4 | Electrical Protective Devices
|  |  | 3.26.5 | Phase-Reversal and Failure Protection
|  |  | 3.26.6 | Control and Operating Circuits
|  |  | 3.20. | Ropes and Rope Connections
| 8.7.3.22.3 | Decrease in Rated Speed |  |  | Major | -
|  |  | 3.4. | Bottom and Top Clearances and Runbys for Cars and Cwts
|  |  | 2.18.2 | Tripping Speeds for Speed Governors
|  |  | 3.16. | Capacity & Loading
|  |  | 3.16.3(b) | Capacity & data plates
|  |  | 2.26.4.1 | Electrical Equipment and Wiring
|  |  | 2.26.4.2 | Drive Machine Controllers for Stopping/Starting/Controlling
| 8.7.3.23 | Hydraulic Equipment |  |  | ò See Below ò
| 8.7.3.23.1 | Alter / Install / Replace |  | Hydraulic Jacks | Major | - | Major
|  |  | 3.18. | Hydraulic Jacks |  |  | see 8.6.3.10.1
| 8.7.3.23.2 | Alter / Install / Replace |  | Plungers | Major | - | Minor A
|  |  | 3.18.1.2 | Roped-Hydraulic Elevator
|  |  | 3.18.2 | Plungers
| 8.7.3.23.3 | Alter / Install / Replace |  | Cylinders | Major | - | Minor A
|  |  | 3.18.3 | Cylinders |  |  | see 8.6.3.10.2
|  |  | 3.18.3 | Cylinder is Altered
|  |  | 3.18.3 | Cylinder is Sleeved | Minor A
|  |  | 3.18.4.1 | Metal Stops and/or Other Means
|  |  | 3.18.1.2 | Roped-Hydraulic Elevator
|  |  | 3.18.2 | Plungers
| 8.7.3.23.4 | Increase in Working Pressure >5% |  |  | Major | -
|  |  | 3.18.(*) | Hydraulic Jacks
|  |  | 3.19.(*) | Valves, Pressure Piping, and Fittings
|  |  | 3.24.1 | Marking Plates
|  |  | 3.24.2 | Tanks
|  |  | 3.24.3 | Atmosphere Storage and Discharge Tanks
|  |  | 3.24.4 | Welding
| 8.7.3.23.5 | Change in Location of Hydraulic Jack |  |  | Major | -
|  |  | Part 3 | Hydraulic Elevators
| 8.7.3.23.6 | Relocation of Hydraulic Machine (Power Unit) |  |  | Minor A | -
|  |  | 3.26.8 | Pressure Switch
| 8.7.3.23.7 | Plunger Gripper |  |  | Minor A | Minor A
|  |  | 3.17.3 | Plunger Gripper
|  |  | 3.1.1(b) | strength of pit floor
|  |  | 3.22.1 | no strike when buffers compressed
CAD
| 8.7.3.23.7 «1 | Removal of Plunger Gripper |  |  | Minor A | -
|  |  | 3.18.3 | Cylinders
|  |  | 3.19.4.7 | Overspeed Valves
|  |  | 3.4.2.1 | Bottom Car Runby
| 8.7.3.24 (a) | Alter / Replace |  | Control Valves | Minor A | - | Minor B
|  |  | 3.19. | Valves, Pressure Piping, and Fittings |  |  | see 8.6.3.11
| 8.7.3.24 (b) | Alter / Replace |  | Relief Valves | Minor A | Minor A | Minor B
|  |  | 3.19. | Valves, Pressure Piping, and Fittings |  |  | see 8.6.3.11
| 8.7.3.24 (b) | Alter / Replace |  | Check Valves | Minor A | Minor A | Minor B
|  |  | 3.19. | Valves, Pressure Piping, and Fittings |  |  | see 8.6.3.11
| 8.7.3.24 (b) | Alter / Replace |  | Pressure Piping or Fittings | Minor A | Minor A | Minor B
|  |  | 3.19. | Valves, Pressure Piping, and Fittings |  |  | see 8.6.3.11
| 8.7.3.25 | Suspension Ropes and Their Connections |  |  | ò See Below ò
| 8.7.3.25.1 | Change in Number of, or Diameter of Ropes |  |  | Major | -
|  |  | 3.20. | Ropes and Rope Connections
PEO to certify retained sheaves w/different ropes are satisfactory
| 8.7.3.25.1 | Change in Material / Grade of Ropes |  |  | Minor A | -
|  |  | 3.20. | Ropes and Rope Connections
PEO to certify retained sheaves w/different ropes are satisfactory
| 8.7.3.25.2 | Addition of Rope Equalizers |  |  | Minor B | Minor B
|  |  | 2.20.5 | Suspension Rope Equalizers
| 8.7.3.26 | Counterweights - Alteration of |  |  | See 8.7.2.22
| 8.7.2.22 | Counterweights |  |  | Minor A | -
| 8.7.2.22.1 |  | Alteration to any part of a cwt except guiding members
|  |  | 2.21. | Counterweights
|  |  | 3.21. | Counterweights
|  |  | 8.7.2.22.2 | Rod Type Counterweights
|  |  | 8.7.2.3 | Location and Guarding of Counterweights
| 8.7.2.22.2 |  | Rod Type Cwt - can retain if:
Minimum of 2 suspension and 2 tie rods
Suspension rods:
|  |  | 2.21.2.1 | Material - Cwt Frames & Rods
|  |  | 2.21.2.3 | Factor of Safety
Tie Rods:
|  |  | 2.21.1.2 | Retention of Weight Sections
| 8.7.2.22.3 |  | Roller or similar guide shoes added |  | mrr |  | mrr
safety jaws cannot touch rails if not activated
| 8.7.3.26 | Counterweights - Addition of |  |  | - | Major
|  |  | 3.4. | Bottom and Top Clearances and Runbys for Cars and Cwts
|  |  | 3.6. | Protection of Spaces below Hoistway
|  |  | 3.14. | Car: Enclosure, Doors, Gates, Illumination
|  |  | 2.14. | Car: Enclosure, Doors, Gates, Illumination
|  |  | 2.14.1.7.1 | car top guard rail to CAD 8.7.2.144
|  |  | 3.15. | Car Frames & Platforms
|  |  | 3.17.2 | Counterweight Safeties
|  |  | 3.18. | Hydraulic Jacks
|  |  | 3.20. | Ropes and Rope Connections
|  |  | 3.21. | Counterweights
|  |  | 8.7.3.3 | Location and Guarding of Counterweights
| 8.7.3.27 | Car Buffers and Bumpers |  |  | Major | - | mrr | Minor B
|  |  | 3.21. | Counterweights
|  |  | 3.22.2(*) | Counterweight Buffers
| 8.7.3.28 | Guide Rails, Supports, and Fastenings (alteration to, or stress increase >5%) |  |  | Major | -
|  |  | 3.23. | Guide Rails, Guide-Rail Supports, and Fastenings
|  |  | 3.28. | Layout Data
| 8.7.3.29 | Alteration to |  | Tanks | Minor B | - | Minor B
|  |  | 3.24. | Hydraulic Machines and Tanks |  |  | see 8.6.3.10.4
| CAD 8.7.3.29«1 | « Addition of Oil Cooler |  |  | Minor B |  | Minor B
|  |  | 8.7.3.8 | Electrical Wiring, Pipes, and Ducts in H/W and M/C rooms
|  |  | 2.7.2 | Maintenance Path and Clearance
|  |  | 3.10. | Guarding of Exposed Auxiliary Equipment
| 8.7.3.30 | Terminal-Stopping Devices |  |  | Minor B | Minor B
|  |  | 3.25. | Terminal-Stopping Devices
| 8.7.3.31 | Operating Devices and Control Equipment |  |  | ò See Below ò
| 8.7.3.31.1 | Top-of-Car Operating Devices |  |  | Minor A | Minor A | mrr | Minor A
|  |  | 3.26.2 | Inspection Operation
| CAD 8.7.3.31«1 | Alteration / Addition of any type of inspection operation |  |  | Minor A | Minor A
|  |  | 2.26.1.4 | Inspection Operation
| CAD 8.7.3.31«2 |  | Addition of Top-of-Car Operating Device (see CAD 3.8.3) |  | - | Minor A
|  |  | 2.26.1.4 | Inspection Operation
8.7.2.15«1,«2
| 8.7.3.31.2 | Car-Leveling or Truck-Zoning Devices |  |  | Minor A | Minor A
|  |  | 3.26.3.2 | Operation in Leveling or Truck Zone
| 8.7.3.31.3 | Alter / Replace |  | Anti-Creep Leveling Device | Minor B | - | Minor B
|  |  | 3.26.3.1 | Anti-Creep Operation |  |  | see 8.6.3.10.5
| CAD 8.7.3.31«3 | « Door By-Pass Switches |  |  | Minor A | Minor A
|  |  | 2.26.1.5 | Inspection Operation with Open Door Circuits
| CAD 8.7.3.31«4 | « Door Monitoring System |  |  | Minor A | Minor A
|  |  | 2.26.5 | System to Prevent Auto Operation w/faulty Door Contacts
| 8.7.3.31.4 | Change in Power Supply |  |  | Major | -
(a) voltage, frequency or # of phases or
(b) AC to DC , DC to AC or
(c) combination of DC & AC, then
electrical to:
|  |  | 3.26.1 | Operating Devices and Control Equipment
|  |  | 3.26.4 | Electrical Protective Devices
|  |  | 3.26.5 | Phase-Reversal and Failure Protection
|  |  | 3.26.6(*) | Control and Operating Circuits
| CAD 8.7.3.31«5 | « Addition of Soft Start |  |  |  | Minor A
|  |  | 2.26.4.1 & 2 | OESC, CSA C22.1 & B44.1 certified
|  |  | 3.26.5 | Phase-Reversal and Failure Protection
| CAD 8.7.3.31«6 | « Addition of Power Efficiency Increasing Device |  |  |  | Minor B
B44.1 certified
|  |  | 2.26.4.1 & 2 | OESC, CSA C22.1 & B44.1 certified
| 8.7.3.31.5 | Controllers
| 8.7.3.31.5(a) | Install / Replace |  | Elevator Controller | Major | - | Major
|  |  | 3.25. | Terminal-Stopping Devices
|  |  | 3.26. | Operating Devices and Control Equipment
|  |  | 3.26.1 | Operating Devices and Control Equipment
|  |  | 3.26.2 | Inspection Operation
|  |  | 3.26.3 | Anti-Creep and Leveling Operation
|  |  | 3.26.4 | Electrical Protective Devices
|  |  | 3.26.5 | Phase-Reversal and Failure Protection
|  |  | 3.26.6 | Control and Operating Circuits
|  |  | 3.26.7 | Recycling Operation for Multiple or Telescopic Plungers
|  |  | 3.26.8 | Pressure Switch
|  |  | 3.26.9 | Low Oil Protection
|  |  | 3.26.10 | Auxiliary Power Lowering Operation
|  | « | 2.7.9.2 | Temperature and Humidity
|  |  | 2.27.2 | when E.P. Is provided
|  |  | 3.27.1 | Phase 1 Emergency Recall Operation after Device Actuation
|  |  | 3.27.2 | Phase 1 Emergency Recall Operation prior to Device Actuation
|  |  | 3.27.3 | Device Acutation at Recall Level
|  |  | 3.27.4 | Device Acutation with Phase II Emergency In-Car in Effect
If FEO previously present or required by OBC;
|  |  | 2.27.3 | Firefighters' Emergency Operation - Automatic Elevators
2.27.3.1 Phase 1 Recall Operation
2.27.3.2 Phase 1 Recall Operation by FAID's
CAD 2.27.3.2.2
2.27.3.3 Phase 2 Emergency In-Car Operation
2.27.3.4 Interruption of Power
2.27.3.5 Multicompartment Elevators
see 8.7.1.2 safety levels shall not be diminished
|  |  | 2.27.4 | FEO: Non Automatic Elevators
|  |  | 2.27.5 | FEO: Automatic Elevators with Designated-Attendant Operation
|  |  | 2.27.6 | FEO: Inspection Operation
|  |  | 2.27.7 | FEO: Operating Procedures
|  |  | 2.27.8 | Switch Keys
|  |  | 2.27.9 | Elevator Corridor Call Station Pictograph
If FEO NOT previously present or required by OBC;
CAD 2.27.3.2.2
2.27.3.1 Provide Phase 1 Manual Recall Operation Only
| CAD 8.7.3.31«7 | Relocation of |  | Elevator Controller (if control wiring disconnected - reconnected) | Major
|  |  | 2.8.2 | Electrical Equipment and Wiring
Electrical testing as per the original design submission tests
| 8.7.3.31.5(b) | Install / Replace |  | Door Controller | Minor A | - | Minor B
|  |  | 2.26.4.1 | Electrical Equipment and Wiring
|  |  | 2.26.4.2 | Drive Machine Controllers for Stopping/Starting/Controlling
| 8.7.3.31.6 | Change in Type of Motion Control |  |  | Major | -
|  |  | 2.11.1(*) | Entrances and Emergency Doors Required
|  |  | 2.11.2 | Types of Entrances
|  |  | 2.11.3 | Closing of Hoistway Doors
|  |  | 2.11.4 | Location of Horizontally Sliding or Swinging H/W Doors
|  |  | 2.11.5 | Projection of Entrances & Equip. Beyond Land'g Sills
|  |  | 2.11.6(*) | Opening of Hoistway Doors
|  |  | 2.11.8 | Weights for Closing or Balancing Doors
|  |  | 2.11.9 | Hoistway Door Locking Devices & Power Operation
|  |  | 2.11.11.8(*) | Hoistway Door Safety Retainers
|  |  | 2.11.12.8 | Pull Straps
|  |  | 2.12.(*) | H/W-Door Locking Devices, Elec. Contacts, H/W Access
2.12.5 Restricted Opening of Hoistway or Car Doors
2.12.6 Hoistway Door Unlocking Devices
2.12.7 Hoistway Access Switches
|  |  | 2.13. | Power Operation of H/W Doors and Car Doors
|  |  | 2.14.(*) | Car: Enclosure, Doors, Gates, Illumination
2.14.1.7 car top railing
|  |  | 8.7.2.27.5(d) | Capacity & Loading
|  |  | 2.17.(*) | Car & Cwt Safeties
|  |  | 2.18.(*) | Speed Governors
|  |  | 3.25. | Terminal Stopping Devices
|  |  | 3.26.(*) | Operating Devices and Control Equipment
|  |  | 2.29. | Identification of Equipment and Floors
|  | « | 2.7.9.2 | Temperature and Humidity
If FEO previously present or required by OBC;
|  |  | 2.27. | Emergency Operation and Signalling Devices
2.27.1 Car Emergency Signalling Devices
2.27.2 Emergency or Standby Power Systems
2.27.3 Firefighters' Emergency Operation: Automatic Elevators
2.27.3.1 Phase 1 Recall Operation
2.27.3.2 Phase 1 Recall Operation by FAID's
CAD 2.27.3.2.2
2.27.3.3 Phase 2 Emergency In-Car Operation
2.27.3.4 Interruption of Power
2.27.3.5 Multicompartment Elevators
see 8.7.1.2 safety levels shall not be diminished
2.27.4 FEO: Non Automatic Elevators
2.27.5 FEO: Automatic Elevators with Designated-Attendant Operation
2.27.6 FEO: Inspection Operation
2.27.7 FEO: Operating Procedures
2.27.8 Switch Keys
If FEO NOT previously present or required by OBC;
CAD 2.27.3.2.2
2.27.3.1 Provide Phase 1 Manual Recall Operation Only
| 8.7.3.31.7 | Change in Type of Operation Control - CPPB, Automatic |  |  | Major | -
|  |  | 2.11.1 | Entrances and Emergency Doors Required
|  |  | 2.11.2 | Types of Entrances
|  |  | 2.11.3 | Closing of Hoistway Doors
|  |  | 2.11.4 | Location of Horizontally Sliding or Swinging H/W Doors
|  |  | 2.11.5 | Projection of Entrances & Equip. Beyond Land'g Sills
|  |  | 2.11.6 | Opening of Hoistway Doors
|  |  | 2.11.7 | Glass in Hoistway Doors
|  |  | 2.11.8 | Weights for Closing or Balancing Doors
|  |  | 2.11.9 | Hoistway Door Locking Devices & Power Operation
|  |  | 2.11.10 | Landing Sill: Guards, Illumination, hinged sills, Tracks
|  |  | 2.11.11 | Entrances, Horizontal Slide Type
|  |  | 2.11.12 | Entrances, Vertical Slide Type
|  |  | 2.11.13 | Entrances, Swing Type
|  |  | 3.11.1 | Protection of Hoistway Landing Openings
|  |  | 3.12.1 | H/W-Door Locking Devices, Elec. Contacts, H/W Access
|  |  | 3.13. | Power Operation of H/W Doors and Car Doors
|  |  | 3.14.(*) | Car: Enclosure, Doors, Gates, Illumination
|  |  | 3.16. | Capacity & Loading
|  |  | 3.25. | Terminal-Stopping Devices
|  |  | 3.26.(*) | Operating Devices and Control Equipment
|  | « | 2.7.9.2 | Temperature and Humidity
|  |  | 3.27. | Emergency Operation and Signaling Devices
3.27.1 PHI Emergency Recall Operation After Device Actuation
(a) low oil protection
(b) plunger follower guide protection
(c) auxiliary power lowering
(d) oil tank temperature shutdown
2.27 Emergency Operation & Signaling Devices
2.27.1 Car Emergency Signalling Devices
2.27.2 Emergency or Standby Power Systems
2.27.3 FEO: Automatic Elevators
CAD 2.27.3.2.2
2.27.4 FEO: Non-Automatic Elevators
2.27.5 FEO: Automatic Elevators w/Attendant
2.27.6 FEO: Inspection Operation
2.27.7 FEO: Operating Procedures
2.27.8 Switch Keys
2.27.9 Elevator Corridor Call Station Pictograph if reqd by OBC
| CAD 8.7.3.31«8 | « Addition of Wander Patient Feature - Change in Operation Control |  |  | Minor B | Minor B
|  |  | 2.11.3.2 | - doors closed when not in use
|  |  | 2.27.3.1.6(l) | - shall not prevent PHI
| CAD 8.7.3.31«9 | « Addition of Restricted Access - Security / Floor Lock Out |  |  | Minor B | Minor B
|  |  | OBC-3.2.6.5(4) | - shall not prevent floor access When on FEO
D.O. Button Remain Operative Under non FEO Conditions, Door Closed When not in Use
|  |  | 2.27.3.1.6(l) | - shall not prevent PHI
|  |  | 2.27.3.3.1(i) | - permit travel to all landings when on PH II
|  |  | 2.11.6.2 | Cannot Lock Out Top& Btm, Designated & Alternate or All Landings in Phase II
|  |  | DR 172/02 | Elevators With Phase II Operation & Floor Button Controlled by Cards/Keys
| 8.7.3.31.8 | Emergency Operation and Signaling Devices
| 8.7.3.31.8(a) | Car Emergency Signaling Devices |  |  | Minor B | Minor B | mrr
|  |  | 2.27.1 | Car Emergency Signaling Devices
| 8.7.3.31.8(b) | Emergency or Standby Power |  |  | Minor B | Minor A
|  |  | 2.27.2 | Emergency Or Standby Power systems
| 8.7.3.31.8(c) | Firefighter's Emergency Operation |  |  | Minor B | Minor A
|  |  | 3.27. | Emergency Operation and Signaling Devices
3.27.1 PHI Emergency Recall Operation After Device Actuation
(a) low oil protection
(b) plunger follower guide protection
(c) auxiliary power lowering
(d) oil tank temperature shutdown
2.27 Emergency Operation & Signaling Devices
2.27.1 Car Emergency Signalling Devices
2.27.2 Emergency or Standby Power Systems
2.27.3 FEO: Automatic Elevators
CAD 2.27.3.2.2
2.27.4 FEO: Non-Automatic Elevators
2.27.5 FEO: Automatic Elevators w/Attendant
2.27.6 FEO: Inspection Operation
2.27.7 FEO: Operating Procedures
2.27.8 Switch Keys
2.27.9 Elevator Corridor Call Station Pictograph if reqd by OBC
CAD
| 8.7.3.31.8«10 | « Emerg. Recall Upgrade - from Manual to Automatic & matching code at time of install |  |  | Minor B
conformance to auto recall based on F.S. at time of install
CAD
| 8.7.3.31.8«11 | « Emerg. Recall Upgrade to comply with a Fire Code Retrofit Order |  |  | Minor B | Minor A
2.27.3 FEO: Automatic Elevators
| 8.7.3.31.9 | Auxiliary Power Lowering Operation |  |  | Minor B | Minor B
|  |  | 3.26.10 | Auxiliary Power Lowering Operation
include testing procedure
| 8.7.3.31.10 | Removal of emergency stop switch on passenger elevators |  |  | Minor B | Minor B
remove all related markings / engravings & provide an in-car stop switch to:
|  |  | 2.26.2.21 | In-car stop switch
|  |  | 2.26.4.3 | Positively Opened Contacts
|  |  | 2.26.9.3.1(a) | single failure does not render In-Car Stop Switch ineffective
|  |  | 3.26.4.2 | deceleration rate <1g, anticreep must still function
| 8.7.3.31.11 | Electrical Protective Devices |  |  | ò See Below ò
| 8.7.2.27.8 | Alteration or Addition of an Electrical Protective Device |  |  | Major | Major | mrr | Major
if device meets 2.26.4.3.2 (PES)
|  |  | 3.26.2 | Electrical Protective Devices - for specified device
| 8.7.2.27.8 | Alteration or Addition of an Electrical Protective Device |  |  | - | Minor A | mrr
if device meets 2.26.4.3.1
|  |  | 3.26.2 | Electrical Protective Devices - for specified device
| 8.7.4 | Alterations to Elevators w/other Types of Driving Machines
| 8.7.4.1 | Rack and Pinion Elevators |  |  | Major | -
|  |  | 4.1. | Rack and Pinion Elevators
| 8.7.4.2 | Screw-Column Elevators |  |  | Major | -
|  |  | 4.2. | Screw-Column Elevators
| 8.7.4.3 | Hand Elevators |  |  | Major | -
| 8.7.4.3.1 | Hoistway Enclosures and Machinery Space |  |  | Major | -
|  |  | 4.3.1 | Hoistways, H/W Enclosures, and Related Construction
|  |  | 4.3.4 | Enclosures for Machines and Control Equipment
| 8.7.4.3.2 | Top Car and Counterweight Clearances |  |  | Major | -
|  |  | 4.3.3 | Top Clearances
| 8.7.4.3.3 | Hoistway Entrances |  |  | Major | -
|  |  | 4.3.6 | Hoistway Entrances
|  |  | 4.3.7 | Hoistway Gates for Landing Openings
|  |  | 4.3.8 | Hoistway-Door & Hoistway Gate Locking Devices
| 8.7.4.3.4 | Car Enclosures |  |  | Major | -
|  |  | 4.3.9 | Car Enclosures
|  |  | 4.3.11 | Car Frames and Platforms
| 8.7.4.3.5 | Car Frame and Platform |  |  | Major | -
|  |  | 4.3.11 | Car Frames and Platforms
|  |  | 4.3.12 | Car Compartments
|  |  | 4.3.13 | Cars Counterbalancing One Another
|  |  | 4.3.16 | Suspension Means
| 8.7.4.3.6 | Capacity and Loading |  |  | Major | -
|  |  | 4.3.14.1 | Minimum Rated Load
|  |  | 4.3.14.2 | Capacity Plate
|  |  | 4.3.19.1 | Drive Machine & Sheaves - Factors or Safety
|  |  | 4.3.19.2 | Driving-Machines
|  |  | 4.3.16 | Suspension Means
| 8.7.4.3.7 | Increase in Rise |  |  | Major | -
|  |  | 4.3.3.1 | Top Car Clearances
|  |  | 4.3.3.2 | Top Counterweight Clearance
|  |  | 4.3.15 | Car Safeties
|  |  | 4.3.16 | Suspension Means
| 8.7.4.3.8 | Guide Rails and Fastenings |  |  | Major | -
|  |  | 4.3.18.1 | Guide Rails - Material and Finish
|  |  | 4.3.18.2 | Strength of Rails and Fastenings
|  |  | 4.3.18.3 | Extension of Guide Rails at Top & Bottom of H/W
| 8.7.4.3.9 | Overhead Beams and Supports |  |  | Major | -
|  |  | 4.3.5.1 | Overhead Beams and Supports
|  |  | 4.3.5.2 | Access to Machines and Sheaves
| 8.7.4.3.10 | Power Attachments |  |  | Major | -
| 8.7.5 | Alterations to Special Application Elevators
| 8.7.5.1 | Inclined Elevators |  |  | Major | -
|  |  | 5.1. | Inclined Elevators
|  |  |  | compliance to specific 5.1 sections based on alteration scope | variance
| 8.7.5.2 | Limited Use/Limited Application Elevators |  |  | See Electric or Hydraulic Elevator
| CAD 8.7.5.2«1 | « | 8.7.2 | Alterations to Electric Elevator & as modified in Section 5.2
| CAD 8.7.5.2«2 | « | 8.7.3 | Alterations to Hydraulic Elevator & as modified in Section 5.2
| 8.7.5.5 | Power Sidewalk Elevators |  |  | Major | -
| 8.7.5.5.1 | Changes in Electrical Wiring or Electrical Equipment |  |  | Major | -
|  |  | 5.5.1.8 | Equipment in Hoistways & Machine Rooms
| 8.7.5.5.2 | Sidewalk Door |  |  | Major | -
|  |  | 5.5.1.11.2 | Horizontal Openings in Sidewalks and Exterior Areas
|  |  | 5.5.1.11.3 | Hinged Type Swing Sidewalk Doors
|  |  | 5.5.1.11.4 | Vertical Lifting Sidewalk Covers
| 8.7.5.5.3 | Change in Car Enclosure, Car Doors, and Gates |  |  | Major | -
|  |  | 5.5.1.14 | Car Enclosure, Car Doors and Gates, Illumination
| 8.7.5.5.4 | Bow-Irons and Stanchions |  |  | Major | -
|  |  | 5.5.1.15.2 | Bow-Irons and Stanchions
| 8.7.5.5.5 | Increase in Rated Load |  |  | Major | -
|  |  | 5.5.1.16 | Capacity and Loading
|  |  | 5.5.1.18 | Speed Governors
|  |  | 5.5.1.21 | Buffers and Bumpers
|  |  | 5.5.1.25.4 | Maximum Rated Speed
| 8.7.5.5.6 | Increase in Rated Speed |  |  | Major | -
|  |  | 5.5.1.15 | Car Frames and Platforms
|  |  | 5.5.1.16 | Capacity and Loading
|  |  | 5.5.1.19 | Suspension Ropes
|  |  | 5.5.1.22 | Guide Rails
| 8.7.5.5.7 | Existing Driving Machine |  |  | Major | -
|  |  | 5.5.1.8 | Equipment in Hoistways & Machine Rooms
|  |  | 5.5.1.9 | Machinery and Sheave Beams, Supports, and Foundations
|  |  | 5.5.1.23 | Driving Machines and Sheaves
|  |  | 5.5.1.25 | Operating Devices and Control Equipment
| 8.7.5.5.8 | Change in Type of Operating Devices and/or Control Equipment |  |  | Major | -
|  |  | 5.5.1.8 | Equipment in Hoistways & Machine Rooms
|  |  | 5.5.1.25 | Operating Devices and Control Equipment
| 8.7.5.6 | Rooftop Elevators |  |  | Major | -
|  |  | 5.6. | Rooftop Elevators
| 8.7.5.7 | Special Purpose Personnel Elevators |  |  | see CAN/CSA B311
| 8.7.6.1 | Alterations to Escalators
| 8.7.6.1.1 | Change to component parts |  |  | mrr | - | mrr
8.6.12.4.1.1 Replacement parts or components
8.6.12.4.1.2 Quality of Work
| 8.7.6.1.1 | Addition of Components or Devices |  |  | see 8.7.6.1 |  | -
see applicable 8.7.6.1 requirements for that device
| 8.7.6.1.2 (a) | Relocation of Escalator |  |  | New | -
|  |  | 6.1. | Escalators
| 8.7.6.1.2 (b) | Repositioning of Escalator |  |  | Major
| CAD 3.18 | « Repositioning of Escalator (within the same building)
|  |  | 6.1.3.3.11 | Guard at ceiling intersection
|  |  | 6.1.3.3.12 | AntiSlide Devices
|  |  | 6.1.3.3.13 | Deck Barricades
|  |  | 6.1.3.4.3 | Guards
|  |  | 6.1.3.6.3 | Adjacent Floor Surfaces
|  |  | 6.1.3.6.4 | Safety Zone
|  |  | 6.1.3.12 | Headroom
|  |  | 6.1.3.13 | Welding
|  |  | 6.1.6.9 | Signs
|  |  | 6.1.7.4.1 | Electrical equipment
|  |  | 8.7.6.1.3 | Protection of Floor Openings
| 8.7.6.1.3 | Protection of Floor Openings |  |  | Minor A | -
|  |  | 6.1.1.1 | Protection Required
| 8.7.6.1.4 | Protection of Trusses and Machinery Spaces Against Fire |  |  | Minor A | -
|  |  | 6.1.2.1 | Protection Required
| 8.7.6.1.5 | Construction Requirements
| 8.7.6.1.5(a) | Construction Requirements - Angle of Inclination |  |  | Major | -
| 8.7.6.1.5(b) | Construction Requirements - Geometry |  |  | Major | -
|  |  | 6.1.3.2 | Geometry
| 8.7.6.1.5(c) | Any Alteration to the Balustrades |  |  | Minor A | Minor A
|  |  | 6.1.3.3 | Balustrades
|  |  | 6.1.3.3.1 | Construction
|  |  | 6.1.3.3.2 | Strength
|  |  | 6.1.3.3.3 | Use of Glass or Plastic
|  |  | 6.1.3.3.4 | Interior Low Deck
|  |  | 6.1.3.3.5 | Loaded Gap between Skirt & Step
|  |  | 6.1.3.3.6 | Skirt Panels
|  |  | 6.1.3.3.7 | Dynamic Skirt Panels
|  |  | 6.1.3.3.8 | Dynamic Skirt Panel Loaded Gap
|  |  | 6.1.3.3.9 | Step/Skirt Performance Index
|  |  | 6.1.3.3.10 | Skirt Deflector Devices
|  |  | 6.1.3.3.11 | Guard at ceiling intersection
|  |  | 6.1.3.3.12 | AntiSlide Devices
|  |  | 6.1.3.3.13 | Deck Barricades
| 8.7.6.1.5(d) | Deflector Devices |  |  | Minor B |  | mrr
|  |  | 6.1.3.3.10 | Skirt Deflector Devices
| 8.7.6.1.6 | Handrails or Handrail System |  |  | Minor A | -
|  |  | 6.1.3.2.2 | Geometry - Handrail
|  |  | 6.1.3.4.1 | Handrails - Type Required
|  |  | 6.1.3.4.2 | Extension Beyond Combplate
|  |  | 6.1.3.4.3 | Guards (hand or finger)
|  |  | 6.1.3.4.4 | Handrails - Splicing
|  |  | 6.1.3.4.6 | Handrail Clearance
|  |  | 6.1.6.3.12 | Handrail Entry Device
|  |  | 6.1.6.4 | Handrail Speed Monitoring Device
| CAD 8.7.6.1«1 | « Addition of Handrail Advertising |  |  | mrr | variance
Variance to 6.1.6.9.2
| 8.7.6.1.7 | Step System - any alteration to the step system |  |  | Major | - | mrr | Minor B
|  |  | 6.1.3.3.5 | Loaded Gap Between Skirt & Step
|  |  | 6.1.3.5 (*) | Steps
|  |  | 6.1.3.6 | Entrance and Egress Ends
|  |  | 6.1.3.8 | Step Wheel Tracks
|  |  | 6.1.3.9.4 | Step
|  |  | 6.1.3.10.4 | Factor of Safety - Steps
|  |  | 6.1.3.11 | Chains
|  |  | 6.1.6.3.3 | Broken Step-Chain Device
|  |  | 6.1.6.3.9 | Step Upthrust Device
|  |  | 6.1.6.3.11 | Step Level Device
|  |  | 6.1.6.3.14 | Step Lateral Displacement Device
|  |  | 6.1.6.5 | Missing Step Device
| 8.7.6.1.8 | Combplates |  |  | Minor A | -
|  |  | 6.1.6.3.13 | Comb-Step Impact Devices
| 8.7.6.1.9 | Trusses and Girders |  |  | Major | -
|  |  | 8.7.1.4 | Welding
|  |  | 6.1.3.7 | Trusses of Girders
|  |  | 6.1.3.9.1 | Structural Load
|  |  | 6.1.3.10.1 | Factor of Safety - Trusses and Supporting Structures
| 8.7.6.1.9 | New Escalator into Existing Trusses |  |  | New | -
|  |  | 6.1. | Escalators
| 8.7.6.1.10 | Step Wheel Tracks |  |  | Major | -
|  |  | 6.1.3.8 | Step Wheel Tracks
|  |  | 6.1.3.9.4 | Step
|  |  | 6.1.3.10.1 | Factor of Safety - Trusses and Supporting Structures
|  |  | 8.7.1.4 | Welding
| 8.7.6.1.11 | Rated Load and Speed |  |  | Major | -
|  |  | 6.1. | Escalators
| 8.7.6.1.12 | Driving Machine, Motor, and Brake
| 8.7.6.1.12(a) | Driving Machine |  |  | Major | -
|  |  | 6.1.3.9.2 | Machinery
|  |  | 6.1.3.10.3 | Factor of Safety - Power Transmission Parts
|  |  | 6.1.4.1 | Limits of Speed
|  |  | 6.1.5.1 | Connection Between Driving Machine and Main Drive Shaft
|  |  | 6.1.5.2 | Driving Motor
|  |  | 6.1.5.3.1 | Escalator Driving-Machine Brake
|  |  | 6.1.5.3.2 | Main Drive Shaft Brake
|  |  | 6.1.6.3.4 | Broken Drive-Chain Device
|  |  | 6.1.6.3.8 | reversal Stop Device
| 8.7.6.1.12(b) | Driving Motor |  |  | Major | -
|  |  | 6.1.3.9.2 | Machinery
|  |  | 6.1.3.10.3 | Factor of Safety - Power Transmission Parts
|  |  | 6.1.4.1 | Limits of Speed
|  |  | 6.1.5.2 | Driving Motor
|  |  | 6.1.5.3.1 | Escalator Driving-Machine Brake
|  |  | 6.1.5.3.2 | Main Drive Shaft Brake
|  |  | 6.1.6.3.2 | Speed Governor
|  |  | 6.1.6.3.8 | reversal Stop Device
|  |  | 6.1.6.3.10 | Disconnected Motor Safety Device
| 8.7.6.1.12(c) | Machine Brake |  |  | Major | -
|  |  | 6.1.3.9.3 | Brake
|  |  | 6.1.3.10.2 | Factor of Safety - Driving Machine Parts
|  |  | 6.1.5.3.1 | Escalator Driving-Machine Brake
| 8.7.6.1.13 | Operating and Safety Devices |  |  | Minor A | Minor A
|  |  | 6.1.6 | Operating and Safety Devices (for that device)
| CAD 8.7.6.1«2 | « Removal of step demarcation lights |  |  | Minor A | - | -
|  |  | 6.1.3.3.5 | Loaded Gap Between Skirt & Step
|  |  | 6.1.3.5.4 | Clearance between Steps
|  |  | 6.1.3.5.5 | Slotting of Steps and Treads
|  |  | 6.1.3.5.6 | Step Demarcation
|  |  | 6.1.3.6.2 | Distinction Between Comb and Step
| 8.7.6.1.14 | Lighting, Access, and Electrical Work |  |  | Minor B | Minor B
|  |  | 6.1.7 | Lighting, Access, and Electrical Work
| 8.7.6.1.15 | Entrance and Egress |  |  | Major | -
|  |  | 6.1.3.6.1 | Combplates
|  |  | 6.1.3.6.2 | Distinction Between Comb and Step
|  |  | 6.1.3.6.3 | Adjacent Floor Surfaces
|  |  | 6.1.3.6.4 | Safety Zone
| 8.7.6.1.16 | Controller |  |  | Major | - | -
|  |  | 6.1.6.10 | Control and Operating Circuits
|  |  | 6.1.6.11 | Electrically Power Safety Devices
|  |  | 6.1.6.12 | Installation of Capacitors.. To Make EPD's Ineffective
|  |  | 6.1.6.13 | Completion of Maintenance Circuits
|  |  | 6.1.6.14 | Escalator Manual Reset
|  |  | 6.1.6.15 | Contractors and Relays for Use in Critical Operating Circuits
| CAD 8.7.6.1«3 | « Controller - Replacement of |  |  | - | - | Major
|  |  | 8.7.6.1.16 | Controller
| CAD 8.7.6.1«4 | Relocation of |  | Controller (if control wiring disconnected - reconnected) | Major
|  |  | 2.8.2 | Electrical Equipment and Wiring
Electrical testing as per the original design submission tests
| CAD 8.7.6.1«5 | « Addition of Soft start |  |  | - | Minor A
for control systems built to B44-00 and later
|  |  | 6.1.7.4 | Electrical Equipment and Wiring
|  |  | 6.1.6.10.1 | Occurrence of a single ground
|  |  | 6.1.6.10.2 | Redundancy to be checked
|  |  | 6.1.6.10.3 | Motors with Static control
for control systems built prior to B44-00
|  |  | 6.1.7.4 | Electrical Equipment and Wiring
| CAD 8.7.6.1«6 | « Addition of Power Efficiency Increasing Device |  |  | - | Minor B
B44.1 certified
|  |  | 2.26.4.1 & 2 | OESC, CSA C22.1 & B44.1 certified
| 8.7.6.2 | Alterations to Moving Walks
| 8.7.6.2.1 | Change to component parts |  |  | mrr | - | mrr
8.6.12.4.1.1 Replacement parts or components
8.6.12.4.1.2 Quality of Work
| 8.7.6.2.1 | Addition of Components or Devices |  |  | see 8.7.6.2 |  | -
see applicable 8.7.6.2 requirements for that device
| 8.7.6.2.2 | Relocation of Moving Walk |  |  | New | -
|  |  | 6.2. | Moving Walks
| 8.7.6.2.3 | Protection of Floor Openings |  |  | Minor A | -
|  |  | 6.2.1.1 | Protection Required
| 8.7.6.2.4 | Protection of Trusses and Machinery Spaces Against Fire |  |  | Minor A | -
|  |  | 6.2.2.1 | Protection of Supports - Protection Required
| 8.7.6.2.5 | Construction Requirements - Angle of Inclination |  |  | Major | -
|  |  | 6.2. | Moving Walks
| 8.7.6.2.5 | Construction Requirements - Geometry |  |  | Major | -
|  |  | 6.2.3.2 | Geometry
| 8.7.6.2.5 | Construction Requirements - Balustrades |  |  | Minor A | Minor A
|  |  | 6.2.3.3 | Balustrades
| 8.7.6.2.6 | Handrails |  |  | Minor A | -
|  |  | 6.2.3.2.3 | Geometry - Handrail
|  |  | 6.2.3.4 | Handrails
|  |  | 6.2.6.3.10 | Handrail Entry Device
|  |  | 6.2.6.4 | Handrail Speed Monitoring Device
| 8.7.6.2.7 | Treadway System |  |  | Major | -
|  |  | 6.2.3.2.3 | Geometry - Handrail
|  |  | 6.2.3.3.5 | Skirtless Balustrade
|  |  | 6.2.3.3.6 | Skirt Panels
|  |  | 6.2.3.5 | Pallet-Type Treadway
|  |  | 6.2.3.6(*) | Belt-Type Treadway
|  |  | 6.2.3.8 | Entrance and Egress Ends
|  |  | 6.2.3.9 | Supporting Structure
|  |  | 6.2.3.10.4 | Pallet
|  |  | 6.2.3.11.4 | Pallet Factor of Safety
|  |  | 6.2.3.11.5 | Belt Factor of Safety
|  |  | 6.2.3.12 | Chains
|  |  | 6.2.6.3.3 | Broken Treadway Device
|  |  | 6.2.6.5 | Missing Pallet Device
|  |  | 6.2.6.3.9 | Pallet Level Device
| 8.7.6.2.8 | Combplates |  |  | Minor A | -
|  |  | 6.2.3.8 | Entrance and Egress Ends
|  |  | 6.2.6.3.11 | Comb-Pallet Impact Devices
| 8.7.6.2.9 | Trusses and Girders |  |  | Major | -
|  |  | 8.7.1.4 | Welding
|  |  | 6.2.3.9 | Supporting Structure
|  |  | 6.2.3.10.1 | Structural Load
|  |  | 6.2.3.12.1 | Trusses & Supports based on max static load
| 8.7.6.2.9 | New Moving Walk into Existing Truss |  |  | New | -
|  |  | 6.2. | Moving Walks
| 8.7.6.2.10 | Track System |  |  | Major | -
|  |  | 6.2.3.9 | Supporting Structure
|  |  | 6.2.3.10 | Rated Load
|  |  | 6.2.3.11.1 | Trusses & Supports based on max static load
|  |  | 8.7.1.4 | Welding
| 8.7.6.2.11 | Rated Load and Speed |  |  | Major | -
|  |  | 6.2. | Moving Walks
| 8.7.6.2.12 | Driving Machine |  |  | Major | -
|  |  | 6.2.3.10.2 | Machinery Load
|  |  | 6.2.3.11.2 | Factor of Safety for Drive Machine Parts
|  |  | 6.2.3.11.3 | Factor of Safety for Power Transmission members
|  |  | 6.2.3.14 | V-Belt Drives
|  |  | 6.2.3.15 | Headroom
|  |  | 6.2.4 | Rated Speed
|  |  | 6.2.5.1 | Connection Between Driving Machine and Main Drive Shaft
|  |  | 6.2.5.3.1 | Moving Walk Driving-Machine Brakes
|  |  | 6.2.5.3.2 | Main Drive Shaft Brake
|  |  | 6.2.6.3.4 | Broken Drive-Chain Device
|  |  | 6.2.6.3.8 | Disconnected Motor Safety Device
| 8.7.6.2.12 | Drive Motor |  |  | Major | -
|  |  | 6.2.3.10.2 | Machinery Load
|  |  | 6.2.3.11.2 | Factor of Safety for Drive Machine Parts
|  |  | 6.2.3.11.3 | Factor of Safety for Power Transmission members
|  |  | 6.2.4 | Rated Speed
|  |  | 6.2.5.2 | Driving Motor
|  |  | 6.2.5.3.1 | Moving Walk Driving-Machine Brakes
|  |  | 6.2.6.3.2 | Speed Governor
|  |  | 6.2.6.3.7 | Reversal Stop Device
|  |  | 6.2.6.3.8 | Disconnected Motor Safety Device
| 8.7.6.2.12 | Machine Brake |  |  | Major | -
|  |  | 6.2.3.10.3 | Brake
|  |  | 6.2.3.11.2 | Factor of Safety for Drive Machine Parts
|  |  | 6.2.3.11.3 | Factor of Safety for Power Transmission members
|  |  | 6.2.5.3.1 | Moving Walk Driving-Machine Brakes
|  |  | 6.2.5.3.2 | Main Drive Shaft Brake
| 8.7.6.2.13 | Operating and Safety Devices |  |  | Minor A | Minor A
|  |  | 6.2.6 | Operating and Safety Devices (for that device)
| 8.7.6.2.14 | Lighting, Access, and Electrical Work |  |  | Minor B | Minor B
|  |  | 6.2.7 | Lighting, Access, and Electrical Work
| 8.7.6.2.15 | Controller - Installed as part of an alteration |  |  | Major | - | -
|  |  | 6.2.6.9 | Control and Operating Circuits
|  |  | 6.2.6.10 | Electrically Power Safety Devices
|  |  | 6.2.6.11 | Installation of Capacitors.. To Make EPD's Ineffective
|  |  | 6.2.6.12 | Completion of Maintenance Circuits
|  |  | 6.2.6.13 | Moving Walk Manual Reset
|  |  | 6.2.6.14 | Contractors and Relays for Use in Critical Operating Circuits
| CAD 8.7.6.2«1 | « Controller - Replacement of |  |  | - | - | Major
|  |  | 8.7.6.1.16 | Controller
| CAD 8.7.6.2«2 | Relocation of |  | Controller (if control wiring disconnected - reconnected) | Major
|  |  | 2.8.2 | Electrical Equipment and Wiring
Electrical testing as per the original design submission tests
| CAD 8.7.6.2«3 | « Addition of Soft start |  |  | - | Minor A
for control systems built to B44-00 and later
|  |  | 6.1.7.4 | Electrical Equipment and Wiring
|  |  | 6.1.6.10.1 | Occurrence of a single ground
|  |  | 6.1.6.10.2 | Redundancy to be checked
|  |  | 6.1.6.10.3 | Motors with Static control
for control systems built prior to B44-00
|  |  | 6.1.7.4 | Electrical Equipment and Wiring
| CAD 8.7.6.2«4 | « Addition of Power Efficiency Increasing Device |  |  | - | Minor B
B44.1 certified
|  |  | 2.26.4.1 & 2 | OESC, CSA C22.1 & B44.1 certified
| 8.7.7 | Alterations to Dumbwaiters and Material Lifts
| 8.7.7.1 | Dumbwaiters and Material Lifts Without Automatic Transfer Devices |  |  | Major | -
|  | Alteration to a Power and Hand Dumbwaiters |  |  | Major | -
|  |  | 7.1. | Power and Hand Dumbwaiters
|  |  | 7.2. | Electric and Hand Dumbwaiters
|  |  | 7.3. | Hydraulic Dumbwaiters
|  | Alteration to a Material Lifts |  |  | Major | -
|  |  | 7.4. | Material Lifts
| CAD 3.9.2 | Lock and Contact upgrade to Interlock |  |  | Minor A | Minor A
CAD 3.9.2
|  |  | 7.4.14* | Hoistway Door Locking Devices
| 8.7.7.1.1 | General Alterations other than 8.7.7.1.2 |  |  | Major | -
|  |  | Part 7 | Dumbwaiters and Material Lifts
| 8.7.7.1.2 | Increase in Rated Load |  |  | Major | -
|  |  | 7.2.(*) | Electric and Hand Dumbwaiters w/o Transfer Devices
|  |  | 7.3.(*) | Hydraulic Dumbwaiters w/o Transfer Devices
|  |  | 7.4. | Material Lifts
|  |  | 7.5. | Electric Material Lifts
|  |  | 7.6. | Hydraulic Material Lifts
| 8.7.7.2 | Addition of Automatic Transfer Device |  |  | Major | -
|  |  | Part 2 | Electric Elevators
|  |  | Part 3 | Hydraulic Elevators
| 8.7.7.3.1 | Material Lifts and Dumbwaiters With Automatic Transfer Devices |  |  | N/A | N/A
exempt if requirements of CAD 2.3(j) are met
| 8.7.7.3.2 | Material Lifts and Dumbwaiters - remove Transfer Device |  |  | New | -
|  |  | 7.1. to 7.3. | for Dumbwaiters
|  |  | 7.4. to 7.6 | Material Lifts w/o Transfer Devices
| 8.7.7.3.3 | Material Lifts altered to an Elevator |  |  | New | -
|  |  | Part 2 | Electric Elevators
|  |  | Part 3 | Hydraulic Elevators
| 8.7.7.3.4 | Material Lift or Dumbwaiter w/ Transfer Device Altered to a D/W |  |  | New | -
|  |  | 7.1. | Power and Hand Dumbwaiters w/Auto Transfer Devices
|  |  | 7.2. | Electric and Hand Dumbwaiters w/o Transfer Devices
|  |  | 7.3. | Hydraulic Dumbwaiters w/o Transfer Devices
Alterations to Freight Platform Lifts
| CAD 8.7.7«1 | « Alteration to a Type 'A' Freight Platform Lift |  |  | Major | -
|  |  | 7.4. | as applicable to Material Lifts Type 'B' 
|  |  | 7.5. | as applicable to Material Lifts Type 'B' 
|  |  | 7.6. | as applicable to Material Lifts Type 'B' 
 excluding requirements related to in-car operating devices & Riders
| CAD 3.9.2 | Lock and Contact upgrade to Interlock |  |  | Minor A | Minor A
CAD 3.9.2
|  |  | 7.4.14* | Hoistway Door Locking Devices
| CAD 8.7.7«2 | « Alteration to a Type 'B' Freight Platform Lift |  |  | Major | -
|  |  | 7.4. | as applicable to Material Lifts Type 'B'
|  |  | 7.5. | as applicable to Material Lifts Type 'B'
|  |  | 7.6. | as applicable to Material Lifts Type 'B'
| CAD 3.9.2 | Lock and Contact upgrade to Interlock |  |  | Minor A | Minor A
CAD 3.9.2
|  |  | 7.4.14* | Hoistway Door Locking Devices

## 8.7.2 Elec
0 | 1 | 2a | 2b | 2c | 3 | 4 | 5 | 6
Conforms to B44 Mark with 'X' | B44-10 Reference Number | Alteration Checklist for Director's Guideline 251-11-r2 Scope of Alteration - B44 - 2010 as amended by CAD 261/13-r1 Part, Section or Requirement |  |  | Type of Alteration Work
[5 empty] | Alteration |  | Replacement with
[5 empty] | Modification Change | Addition | Same | Different Make/Model
|  | Job Reference: |  |  | Type of Submission Required
| 8.7.1.2 | Alterations not specifically covered in 8.7
|  |  | 1.2 | Level of safety shall not be diminished
| 8.7.1.4 | Welding
|  |  | 8.8 | Welding
|  |  | 8.7.1.5 | Design / Weld Engineer
| 8.7.1.7 | Repairs and Replacements
|  |  | 8.6.2 | for repairs
|  |  | 8.6.3 | for replacements
| 8.7.2 | Alterations to Electric Elevators
| 8.7.2.1 | Hoistway Enclosures |  |  | Major | Major
| 8.7.2.1.1 | Hoistway Enclosure Walls |  |  | Major | Major
|  |  | 2.1.1 | Hoistway Enclosures
|  |  | 2.1.5 | Windows and Skylights
|  |  | 2.1.6 | Projections, Recesses, and Setbacks in H/W
|  |  | 2.5. | Horizontal Car and Counterweight Clearances
|  |  | 2.7.3.4.6 | Access Doors and Openings
|  | « | 2.7.3.4.7 | Access Doors and Openings
|  |  | 2.8. | Equipment in Hoistways,Machinery Spaces, Machine Rooms, Control Spaces, and Control Rooms
|  |  | 8.7.2.10 | Entrances and Hoistway Openings (if change includes an entrance)
|  |  | 2.11.1 | Entrances and Emergency Doors Required (if blind H/W)
| 8.7.2.1.2 | Addition of Elevator to Existing Hoistway |  |  | - | New
|  |  | B44-2010 | New Installation
|  |  | 2.5. | Horizontal Car and Counterweight Clearances
| 8.7.2.1.3 | Construction at Top of Hoistway |  |  | Major | Major
|  |  | 2.1.2.1 | Construction at Top of the Hoistway
|  |  | 2.1.3 | Floor Over Hoistways
|  |  | 8.7.2.4 | Vertical Car & Cwt Clearances & Runbys
| 8.7.2.1.4 | Construction at Bottom of Hoistway |  |  | Major | Major
|  |  | 2.1.2.2 | Construction at Bottom of the Hoistway
|  |  | 2.1.2.3 | Strength of Pit Floor
|  |  | 2.2. | Pits
|  |  | 8.7.2.4 | Vertical Car & Cwt Clearances & Runbys
| 8.7.2.1.5 | Control of Smoke and Hot Gases |  |  | Major | Major
|  |  | 2.1.4 | Control of Smoke and Hot Gases
| 8.7.2.2 | Pits | see other alterations below for non Major Alterations |  | Major | -
|  |  | 2.2. | Pits
|  |  | 2.1.2.3 | Strength of Pit Floor
|  |  | 8.7.2.4 | Vertical Car & Cwt Clearances & Runbys
| 8.7.2.2 | Pit Drains & Sumps |  |  | Minor B | Minor B
|  |  | 2.2.2. | Pit Drains
| 8.7.2.2 | Pit Guards |  |  | Minor B | Minor A
|  |  | 2.2.3 | Guards Between Adjacent Pits
| 8.7.2.2 | Pit Access |  |  | Minor B | Minor A
|  |  | 2.2.4 | Pit Access
| 8.7.2.2 | Pit Illumination |  |  | Minor B | Minor B
|  |  | 2.2.5 | Illumination of Pits
| 8.7.2.2 | Pit Stop Switches |  |  | Minor B | Minor A
|  |  | 2.2.6 | Stop Switches
| 8.7.2.2 | Pit Depth |  |  | Minor B | Minor A
|  |  | 2.2.7 | Minimum Pit Depths Required
| 8.7.2.2 | Access to Underside of Car |  |  | Minor B | Minor A
|  |  | 2.2.8 | Access to Underside of Car
| 8.7.2.3 | Location and Guarding of Counterweights |  |  | Major | Major
|  |  | 2.3. | Location and Guarding of Counterweights
|  |  | 2.5.1.2 | Between Car & Cwt and Cwt Guard
|  |  | 2.6. | Protection of Space below H/W
| 8.7.2.4 | Vertical Car and Counterweight Clearances and Runbys (no reduction allowed) |  |  | Major | -
|  |  | 2.4. | Vertical Clearances & Runbys for Cars & Cwts
|  |  | 8.7.2.17.1 | Increase or Decrease in Rise
|  |  | 8.7.2.17.2 | Increase in Rated Speed
|  |  | 8.7.2.25.2 | Change in Location of Driving Machine
| 8.7.2.5 | Horizontal Car and Counterweight Clearances (no reduction allowed) |  |  | Major | -
|  |  | 2.5. | Horizontal Car and Counterweight Clearances
|  |  | 8.7.2.17.2 | Increase in Rated Speed
| 8.7.2.6 | Protection of Spaces Below Hoistways |  |  | Minor B | Major
|  |  | 2.6. | Protection of Space below H/W
| 8.7.2.7 | Machinery Spaces, Machine Rooms Control Spaces and Control Rooms |  |  | ò See Below ò
| 8.7.2.7.1 | Enclosures - other than specifics of 8.7.2.7.2 to 8.7.2.7.7
|  |  | 2.7. (& 3.7.) | New - Machinery Spaces, Machine Rooms Control Spaces & Control Rooms | - | Major
|  |  | 2.7. (& 3.7.) | Altered- Machinery Spaces, Machine Rooms Control Spaces & Control Rooms | Minor A | -
|  |  | OESC | Electrical Equipment Clearances | Minor B | -
| 8.7.2.7.2 | Means of Access |  |  | Minor B | -
|  |  | 2.7.3.1 | General Requirements
|  |  | 2.7.3.2 | Access Across Roofs
|  |  | 2.7.3.3 | Means of Access
| 8.7.2.7.3 | Access Doors and Openings |  |  | Minor B | Minor B | mrr
|  |  | 2.7.3.4 | Access Doors and Openings
|  |  | 2.7.3.5 | Stop Switch for Machinery Space or Control Spaces
| 8.7.2.7.4 | Headroom (no reduction) |  |  | Minor B | Minor B
|  |  | 2.7.4 | Headroom in Machine Rooms/Spaces, Control Room/Spaces
| 8.7.2.7.5 | Windows and Skylights |  |  | Minor B | Minor B
2.1.5
| 8.7.2.7.6 | Lighting (no reduction) |  |  | Minor B | Minor A
|  |  | 2.7.9.1 | Lighting
| 8.7.2.7.7 | Ventilation |  |  | Minor B | Minor B
|  |  | 2.7.9.2 | Temperature & Humidity
| CAD 8.7.2.7«1 | Addition of Elevator Equipment Guarding |  |  | Minor A (per m/c rm) |  | mrr | mrr
|  | (a) | 2.7.2 | Maintenance Path and Clearance
|  | (b) | 2.7.3.4.2 | Size of doors and openings in cage style enclosures (750x2030)
|  | (c) | 2.10.1 | Guarding of Equipment
|  | (d) |  | openable/removable only with tools
|  | (e) |  | operating/work instruction for accessing equipment
|  | (f) |  | clearances in front of electrical control equipment (1000mm)
or clearance required at time of original control installation
|  | (g) |  | access in front of / space to operate main disconnect (1000mm),
or (750mm) if permitted at time of original installation
|  | (h) |  | Installation by registered contractor
|  | (i) |  | designed to be handled by one person
| 8.7.2.8 | Electrical Equipment, Wiring, Pipes, and Ducts in H/W's &M/C Rooms |  |  | Minor B | Minor B | mrr | Minor B
|  | Installation of New (electrical equipment, wiring, raceways, cables, pipes, ducts) |  |  | - | Minor B
also installation of Monitoring Equipment, HVAC
|  |  | 2.8. | Equipment in Hoistways and Machine Rooms
CSA Labeling (or equivalent)
OESC, CSA C22.1 as required
|  | Alteration of Existing (electrical equipment, wiring, raceways, cables, pipes, ducts…) |  |  | Minor B | -
|  |  | 2.8. | Equipment in Hoistways and Machine Rooms
| 8.7.2.9 | Machinery and Sheave Beams, Supports, and Foundations |  |  | Major | Major
New/Relocated Machinery & Sheave Beams, Supports, Foundation
|  |  | 2.9. | Machinery & Sheave Beams, Supports, Foundation
adequacy of building structure verified by P.Eng.
Building reactions increased by more than 5%
|  |  | 2.9. | Machinery & Sheave Beams, Supports, Foundation
adequacy of building structure verified by P.Eng.
| 8.7.2.10 | Entrances and Hoistway Openings |  |  | Major | Major | see below
| 8.7.2.10.1 | General Requirements |  |  | Major | -
| 8.7.2.10.1(a) | General Requirements - All New Entrances |  |  | Major | - | Major | Major
|  |  | 2.11. | Protection of H/W Openings
|  |  | 2.12. | H/W-Door Locking Devices, Elec. Contacts, H/W Access
|  |  | 2.13. | Power Operation of H/W Doors and Car Doors
|  |  | 2.29.2 | Identification of Floors
| 8.7.2.10.1(b) | General Requirements - New Entrances w/Existing Entrances |  |  | - | Major
|  |  | 2.11.2 | Types of Entrances
|  |  | 2.11.3 | Closing of Hoistway Doors
|  |  | 2.11.4 | Location of Horizontally Sliding or Swinging H/W Doors
|  |  | 2.11.5 | Projection of Entrances & Equip. Beyond Land'g Sills
|  |  | 2.11.6 | Opening of Hoistway Doors
|  |  | 2.11.7 | Glass in Hoistway Doors
|  |  | 2.11.8 | Weights for Closing or Balancing Doors
|  |  | 8.7.2.10.5 | Marking of Entrance Assemblies
Entire installation to meet:
|  |  | 2.11.6 | Opening of Hoistway Doors
|  |  | 2.12. | H/W-Door Locking Devices, Elec. Contacts, H/W Access
|  |  | 2.13. | Power Operation of H/W Doors and Car Doors
|  |  | 2.29.2 | Identification of Floors
| 8.7.2.10.1(c) | General Requirements - Alteration to H/W Entrance |  |  | Major | -
|  |  | 2.11.3 | Closing of Hoistway Doors
|  |  | 2.11.5 | Projection of Entrances & Equip. Beyond Land'g Sills
|  |  | 2.11.7 | Glass in Hoistway Doors
|  |  | 2.11.8 | Weights for Closing or Balancing Doors
|  |  | 8.7.2.10.5 | Marking of Entrance Assemblies
Entire installation to meet:
|  |  | 2.12. | H/W-Door Locking Devices, Elec. Contacts, H/W Access
|  |  | 2.13. | Power Operation of H/W Doors and Car Doors
|  |  | 2.29.2 | Identification of Floors
| 8.7.2.10.1(d) | General Requirements - Emergency Doors (added or altered) |  |  | Major | Major
|  |  | 2.11.1 | Entrances and Emergency Doors Required
|  |  | 8.7.2.10.5 | Marking of Entrance Assemblies
| 8.7.2.10.1(e) | General Requirements - Access Openings (installed for cleaning) |  |  | Major | Major
|  |  | 2.11.1.4 | Access Opening for Cleaning of Car & H/W Enclosure
|  |  | 8.7.2.10.5 | Marking of Entrance Assemblies
| 8.7.2.10.2 | Horizontal Slide-Type Entrances - new entrance and components to meet: |  |  | Major | Major | see below
|  |  | 8.7.2.10.1 | Entrances & H/W Openings - General Req'mts |  |  | Major
|  |  | 2.11.11 | Entrances, Horizontal Slide Type
Installed New components to meet:
| sills (a) |  | 2.11.10.1 | Landing-Sill Guards | Minor B |  | Minor B
|  |  | 2.11.11.1 | Landing Sills
|  |  | 2.11.11.6 | Bottom Guides
| hanger /track (b) |  | 2.11.11.2 | Hanger Tracks, and Track Supports | Minor B |  | Minor B
| frame (c) |  | 2.11.11.3 | Entrance Frames | Minor A |  | Minor A
|  |  | 2.11.11.5.1 | Panel Overlap
|  |  | 2.11.11.5.2 | Panel Gaps Clearances
|  |  | 2.11.11.5.3 | Pockets in Strike Jamb
|  |  | 8.7.2.10.5 | Marking of Entrance Assemblies
| hangers (d) |  | 2.11.11.4 | Hangers | Minor B |  | Minor B
| panels (e) |  | 2.11.11.5(*) | Panels | Minor A |  | Minor A
|  |  | 2.11.11.6 | Bottom Guides
|  |  | 2.11.11.7 | Multipanel Entrances
|  |  | 8.7.2.10.5 | Marking of Entrance Assemblies
| retainers (f) |  | 2.11.11.8 | Hoistway Door Safety Retainers | Minor B |  | Minor B
| 8.7.2.10.3 | Vertical-Slide-Type Entrances - new entrance and components to meet: |  |  | Major | Major | see below
|  |  | 8.7.2.10.1 | Entrances & H/W Openings - General Req'mts |  |  | Major
|  |  | 2.11.12 | Entrances, Vertical Slide Type
Installed New components to meet:
| sills (a) |  | 2.11.10.3 | Hinged Hoistway Landing Sills | Minor B |  | Minor B
|  |  | 2.11.12.1 | Landing Sills
| frames (b) |  | 2.11.12.2 | Entrances Frames | Minor B |  | Minor B
|  |  | 8.7.2.10.5 | Marking of Entrance Assemblies
| rails (c) |  | 2.11.12.3 | Rails | mrr |  | mrr
| panels (d) |  | 2.11.12.3 | Rails | Minor A |  | Minor A
|  |  | 2.11.12.4 | Panels
|  |  | 2.11.12.5 | Guides
|  |  | 2.11.12.6 | Counterweighting or Counterbalancing
|  |  | 2.11.12.8 | Pull Straps
|  |  | 8.7.2.10.5 | Marking of Entrance Assemblies
| guides (e) |  | 2.11.12.5 | Guides | mrr |  | mrr
| sill guard (f) |  | 2.11.12.7 | Sill Guards
| straps (g) |  | 2.11.12.8 | Pull Straps
| 8.7.2.10.4 | Swing-Type Entrances - new entrance and components to meet: |  |  | Major | Major | see below
|  |  | 8.7.2.10.1 | Entrances & H/W Openings - General Req'mts |  |  | Major
|  |  | 2.11.13 | Entrances, Swing Type
Installed New components to meet:
| sills (a) |  | 2.11.10.1 | Landing-Sill Guards | Minor B |  | Minor B
|  |  | 2.11.10.3 | Hinged Hoistway Landing Sills
|  |  | 2.11.13.1 | Landing Sills
| frames (b) |  | 2.11.13.2 | Entrance Frames | Minor B |  | Minor B
|  |  | 2.11.13.4 | Hinges
|  |  | 8.7.2.10.5 | Marking of Entrance Assemblies
| panels (c) |  | 2.11.13.3 | Panels | Minor B |  | Minor B
|  |  | 2.11.13.4 | Hinges
|  |  | 2.11.13.5 | Marking
|  |  | 8.7.2.10.5 | Marking of Entrance Assemblies
| hinges (d) |  | 2.11.13.4 | Hinges | mrr |  | mrr
| 8.7.2.10.5 | Marking of Entrance Assemblies (Alteration to an Entrance Door Panel) |  |  | Major | Major
Fire Protection Rating not less then existing entrance
|  |  | 8.7.2.10.5(a) | NBCC requirements
| CAD 8.7.2.10«1 | « Removing Service To a Floor |  |  | Minor B
Bolt entrances shut
Remove Interlock From Safety String
Remove COP Floor Button
|  |  | 2.11.6.2 | Cannot Lock Out Top/Btm, Designated/Alternate, All Landing in Phase II
|  |  | 2.12.7 | H/W Access Switches - if floor was previously the access location
| CAD 8.7.2.10«2 | « Door Safety Retainers |  |  | Minor B | Minor A | mrr | Minor B
|  |  | 2.11.11.8 | Hoistway Door Safety Retainers
| 8.7.2.11 | Hoistway Door-Locking Devices, Access Switches & Parking Devices |  |  | ò See Below ò
| 8.7.2.11.1 | Interlocks |  |  | - | Major | mrr | Minor B
|  |  | 2.12.1 | General
|  |  | 2.12.2 | Interlocks
|  |  | 2.12.4 | Listing/Certification Locking Devices
|  |  | 2.12.5 | Restricted Opening of H/W or Car Door (n/a for column 5,6) |  |  | n/a
|  |  | 2.12.6 | Hoistway Door Unlocking Devices (n/a for column 5,6) |  |  | n/a
|  |  | 2.12.7 | Hoistway Access Switches (n/a for column 5,6) |  |  | n/a
| 8.7.2.11.2 | Mechanical Locks and Electric Contacts |  |  | - | Major | mrr | Minor B
|  |  | 2.12.1 | General
|  |  | 2.12.3 | H/W Door Combination Mechanical Locks & Contacts
|  |  | 2.12.4 | Listing/Certification Locking Devices
|  |  | 2.12.6 | Hoistway Door Unlocking Devices
| 8.7.2.11.3 | Parking Devices |  |  | Minor A | Minor A
|  |  | 8.7.2.11.3 | requirements specified
| 8.7.2.11.4 | Access Switches and Unlocking Devices
| 8.7.2.11.4 (a) | Addition of Unlocking Devices |  |  | - | Minor B | mrr
|  |  | 2.12.6 | Hoistway Door Unlocking Devices
| 8.7.2.11.4 (b) | Addition of Access Switches |  |  | - | Minor A | mrr
|  |  | 2.12.7 | Hoistway Access Switches
|  |  | 2.26.1.4 | Inspection Operation
| 8.7.2.11.5 | Restricted Opening of H/W or Car Doors of Passenger Elevators (Restrictors) (Altered or Installed) |  |  | Minor B | Minor B | mrr | Minor B
|  |  | 2.12.5 | Restricted Opening of H/W or Car Door
| 8.7.2.12 | Power Operation of Hoistway Doors (Addition / Alteration to Power Open or Close) |  |  | Minor A | Minor A
|  |  | 8.7.2.10.1 | Entrances & H/W Openings - General Req'mts
|  |  | 8.7.2.10.2 | Horizontal Slide-Type Entrances
|  |  | 8.7.2.10.3 | Vertical Slide-Type Entrances
|  |  | 8.7.2.10.5 | Marking of Entrance Assemblies
|  | « | 2.13. | Power Operation of Hoistway Doors and Car Doors
| CAD 8.7.2.12«1 | « Replacement of Door Operator |  |  | - | - | mrr | Minor B
|  |  | 2.13. | Power Operation of Hoistway Doors and Car Doors
8.7.2.15«1,«2
| 8.7.2.13 | Door Reopening Device (Safety Edge) (Altered or Added or replaced) |  |  | Minor B | Minor B | mrr | Minor B
|  |  | 2.13.4 | Closing Limitations for Power Operated HS Doors & Gates |  |  | see
|  |  | 2.13.5 | Reopening Device for Power Operated Car Doors or Gates |  |  | 8.6.3.8
if FEO provided, door opening & closing to PHI &II at time of install
8.7.2.15«1,«2
| 8.7.2.14 | Car Enclosures, Car Doors and Gates, and Car Illumination |  |  | ò See Below ò
| 8.7.2.14.1 | Installation of New Car Enclosure |  |  | Major | -
|  |  | 2.14. | Car: Enclosure, Doors, Gates, Illumination
|  |  | 2.15. | Car Frames & Platforms
|  |  | 2.17 | Car and counterweight safeties
|  |  | 8.7.2.15.1 | Alterations to Car Frames and Platforms
| 8.7.2.14.2 | Alteration to Existing Cars |  |  | Minor A | Minor A
| 8.7.2.14.2(a) | Car Enclosure - Securing of Enclosures |  |  | Minor A | Minor A
|  |  | 2.14.1.2 | Securing of Enclosures
| 8.7.2.14.2(b) | Top Emergency Exit (Altered or Added) |  |  | Minor B | Minor B
|  |  | 2.14.1.5 | Top Emergency Exits
| 8.7.2.14.2(c) | Installation of Glass |  |  | Minor B | Minor B
|  |  | 2.14.1.8 | Glass in Elevator Cars
|  |  | 2.14.1.8.1 | Enclosures include glass
|  |  | 2.14.1.8.2 | Lining of Walls or Ceilings include glass |  |  | mrr
|  |  | 2.14.1.8.3 | Marking of each Glazing Panel
| 8.7.2.14.2(d) | Specific Equipment in Elevator Car |  |  | Minor B | Minor B
|  |  | 2.14.1.9 | Equipment Inside Cars
|  |  | (a) | Handrails
|  |  | (b) | fastening devices for protective linings
|  |  | (c) | ceiling mounted hooks/tracks
|  |  | (d) | picture frames display boards, plaques <38mm protrusion
secured to 2.14.1.2
material to 2.14.2.1
|  |  | (e) | conveyor tracks in freights
|  |  | (f ) | heating or cooling equipment
8.7.2.15«1,«2
| CAD 8.7.2.14«1 | « Car operating station |  |  | Minor B | Minor B | mrr | Minor B
verify inspection operation 'if provided'
verify stop sw
verify switches operate as before (eg. FS, FEO, Access)
8.7.2.15«1,«2
| CAD 8.7.2.14«2 | « video cameras / surveillance equipment / video monitors |  |  | Minor B | Minor B
|  |  | 2.8.2.1 | electrical equipment & wiring
|  |  | 2.14.1.2.3 | securing of enclosure equipment
|  |  | 2.14.2.4 | Headroom in Elevator Cars
8.7.2.15«1,«2
| CAD 8.7.2.14«3 | « other equipment |  |  | Variance
| 8.7.2.14.2(e) | Side Emergency Exits - Secured Shut |  |  | Major | -
| 8.7.2.14.2(f) | Car Ventilation |  |  | Minor B | -
|  |  | 2.14.2.3 | Ventilation
| 8.7.2.14.2(g) | Car Illumination |  |  | Minor B | Minor B
|  |  | 2.14.7 | Illumination of Cars and Lighting Fixtures
| 8.7.2.14.2(h) | Partitions Installed in Elevator Cars |  |  | Major | Major
|  |  | 2.16.1.2 | Use of Partitions for Reducing Inside Net Platform Area
| 8.7.2.14.2(i) | Installation of Car Door or Gate, Installation to meet: |  |  | Major | Major
|  |  | 2.14.4 | Passenger and Freight Car Doors/Gates, General Requirements
|  |  | 2.14.5 | Passenger Car Doors
|  |  | 2.14.6 | Freight Elevator Car Doors and Gates
| 8.7.2.14.4 | Car Enclosure / Car Door or Car Gates |  |  | ò See Below ò
| 8.7.2.14.4 | Alteration to Car Enclosure other than 8.7.2.14.2 - Enclosure Materials
|  |  | 2.14. | Car: Enclosure, Doors, Gates, Illumination
enclosure material flame ratings shall not be diminished
|  |  |  | 2.14.1.7 car top railing - see CAD 8.7.2.14«4 |  | Minor A
|  |  |  | 2.14.7.1.3 auxiliary lighting |  | Minor B
|  |  |  | 2.14.7.1.4 car top light & outlet |  | Minor B
|  | « |  | CAD 8.7.2.15«1 | Minor B |  | Minor B
or
|  | « |  | CAD 8.7.2.15«2 | Minor A |  | Minor A
| 8.7.2.14.4 | Alteration to Car Door or Car Gates other than 8.7.2.14.2 |  |  | Minor A | Minor A
|  |  | 2.14. | Car: Enclosure, Doors, Gates, Illumination
2.14.1.7 car top railing
2.14.7.1.3 auxiliary lighting
2.14.7.1.4 car top light & outlet
| O.Reg.209/01s30 | « Relocation of Elevator License to remote location |  |  | Minor B† | -
| CAD 8.7.2.14«4 | « Car Top Guard Rail |  |  | Minor B | Minor A | - | Minor A
|  | CAD | 8.7.2.14«4(a) | Standard Guardrail (to CAD 8.7.2.14«4(a), 2.14.1.7 & OBC)
or
|  | CAD | 8.7.2.14«4(b) | Foldable Guardrail (to CAD 8.7.2.14«4(b), 2.14.1.7 & OBC)
car top run buttons not enabled until extended
normal operation not enabled until stowed
electrical limits to ensure car top clearance in overhead
minor A submission template
|  |  | 8.7.2.15«1,«2 | car weighed prior to alteration
include testing procedure
include revised electrical schematics
| 8.7.2.15 | Car Frames and Platforms |  |  | ò See Below ò
| 8.7.2.15.1 | Alterations to Car Frames and Platforms |  |  | Major | - | Major
|  |  | 2.15. | Car Frames & Platforms
| CAD 8.7.2.15«1 | « Decrease Deadweight <5% or Increase Deadweight of Car (115 kg or Less) |  |  | Minor B | Minor B
|  | CAD | 8.7.2.15«1(a) | cars weighed prior to alteration
|  | CAD | 8.7.2.15«1(b) | In/Out weights recorded or cars weighed after alteration
|  | CAD | 8.7.2.15«1(c) | weight change recorded on auxilliary data tag
|  | CAD | 8.7.2.15«1(e) | testing prior to operation to ensure security of interior finishes
| CAD 8.7.2.15«2 | « Increase Deadweight of Car (>115 kg to 5%) |  |  | Minor A | Minor A
|  | CAD | 8.7.2.15«1
engineering assessment of related items affected by weight change
| 8.7.2.15.2 | Increase or Decrease in Deadweight of Car (Car Wt+Rated Load> 5%) |  |  | Major | -
|  |  | 2.15.(*) | Car Frames & Platforms - «apron guard to ED CAD/as pit permits
|  |  | 2.15.9 | Platform Guards (Aprons)
|  |  | 2.16. | Capacity & Loading
|  |  | 2.17. | Car & Cwt Safeties
|  |  | 2.18. | Speed Governors
|  |  | 2.20. | Suspension Ropes & Connections
|  |  | 2.21.(*) | Counterweights
|  |  | 2.22.(*) | Buffers & Bumpers
|  |  | 2.23. | Car & Cwt Guides Rails, Guide Rail Support, Fastenings
|  |  | 2.24.(*) | Driving Machines & Sheaves
|  |  | 8.7.2.9 | Machinery and Sheave Beams, Supports, Foundations
|  | CAD | 8.7.2.15«1(a) to (e)
| 8.7.2.16 | Capacity, Loading, and Classification |  |  | Major | -
| 8.7.2.16.1 | Change in Type of Service: Passenger to Freight OR Freight to Passenger |  |  | Major | -
|  |  | 2.11.1 | Entrances and Emergency Doors Required
|  |  | 2.11.2 | Types of Entrances
|  |  | 2.11.3 | Closing of Hoistway Doors
|  |  | 2.11.5 | Projection of Entrances & Equip. Beyond Land'g Sills
|  |  | 2.11.6 | Opening of Hoistway Doors
|  |  | 2.11.7 | Glass in Hoistway Doors
|  |  | 2.11.8 | Weights for Closing or Balancing Doors
|  |  | 2.12. | H/W-Door Locking Devices, Elec. Contacts, H/W Access
|  |  | 2.13. | Power Operation of H/W Doors and Car Doors
|  |  | 2.22 (*) | Buffers & Bumpers
|  |  | 2.14. | Car: Enclosure, Doors, Gates, Illumination
|  |  | 2.14.1.7.1 | car top guard rail to CAD 8.7.2.144
|  |  | 2.15.(*) | Car Frames & Platforms - «apron guard to ED CAD/as pit permits
|  |  | 2.16. | Capacity & Loading
|  |  | 2.17.(*) | Car & Cwt Safeties
|  |  | 2.18.(*) | Speed Governors
|  |  | 2.19. | Ascending Car Overspeed & Unintended Car Movement Protection
|  |  | 2.20. | Suspension Ropes & Connections
|  |  | 2.24.(*) | Driving Machines & Sheaves
|  |  | 2.25. | Terminal Stopping Devices
|  |  | 2.26. | Operating Devices and Control Equipment
|  |  | 2.27. | Emergency Operation & Signaling Devices
2.27.1 Car Emergency Signalling Devices
2.27.2 Emergency or Standby Power Systems
2.27.3 FEO: Automatic Elevators
CAD 2.27.3.2.2
2.27.4 FEO: Non-Automatic Elevators
2.27.5 FEO: Automatic Elevators w/Attendant
2.27.6 FEO: Inspection Operation
2.27.7 FEO: Operating Procedures
2.27.8 Switch Keys
2.27.9 Elevator Corridor Call Station Pictograph if reqd by OBC
| 8.7.2.16.2 | Change in Class of Loading: [from any class to any other class ie A, B, C1, C2, C3] |  |  | Major | -
|  |  | 2.16.2 | Minimum Rated Load for Freight Elevators
|  |  | 8.7.2.16.4 | Increase in Rated Load
| 8.7.2.16.3 | Carrying of Passengers on Freight Elevators |  |  | Major | -
|  |  | 2.16.4 | Carrying of Passengers on Freight Elevators
|  |  | 2.16.4.1 | not accessible to general public
|  |  | 2.16.4.2 | rated load not less than required by 2.16.1
|  |  | 2.16.4.3 | conforms to 2.16.8 Passenger Overload in Down Direction
|  |  | 2.16.4.4 | H/W entrances to 2.12.1.1 & 2.11.2.1 or 2.11.2.2(e)
|  |  | 2.16.4.5 | car doors to 2.14.5 Passenger Car Doors
|  |  | 2.16.4.6 | car enclosure openings to 2.14.2.2 Prohibited Openings
|  |  | 2.16.4.7 | conforms to 2.12.5 Restricted Opening of H/W or Car Door
|  |  | 2.16.4.8 | Fs for suspension ropes to Table 2.20.3
|  |  | 2.16.4.9 | Power Operated vertical doors to 2.13.3.4
|  |  | « | apron guard to ED CAD or extent pit permits
|  |  | « | 2.16.5 Signs Required in Freight Elevator Cars
| 8.7.2.16.4 | Increase in Rated Load |  |  | Major | -
Car doors or gates shall be provided at all car entrances
New Car doors and gates to: 2.14.4, 2.14.5, 2.14.6
|  |  | 2.14.4 | Passenger & Frt Car Doors & Gates, General Req'mts
|  |  | 2.14.5 | Passenger Car Doors
|  |  | 2.14.6 | Freight Elevator Car Doors and Gates
|  |  | 2.15.(*) | Car Frames & Platforms- «apron guard to ED CAD/as pit permits
|  |  | 2.16. | Capacity & Loading
|  |  | 2.17. | Car & Cwt Safeties
|  |  | 2.18.(*) | Speed Governors
|  |  | 2.19. | Ascending Car Overspeed & Unintended Car Movement Protection
|  |  | 2.20. | Suspension Ropes & Connections
|  |  | 2.21.(*) | Counterweights
|  |  | 2.22.(*) | Buffers & Bumpers
|  |  | 2.23. | Car & Cwt Guides Rails, Guide Rail Support, Fastenings
|  |  | 2.24. | Driving Machines & Sheaves
|  |  | 2.26.1.4 | Inspection Operation
|  |  | 2.26.1.5 | Inspection Operation with Open Door Circuits
|  |  | 2.26.5 | Monitor & Prevent Automatic Operation w/ Faulty Door Contacts
|  |  | 8.7.2.9 | Machinery and Sheave Beams, Supports, Foundations
| 8.7.2.17 | Change in Rise or Rated Speed |  |  | Major | -
| 8.7.2.17.1 | Increase or Decrease in Rise |  |  | Major | -
|  |  | 2.25. | Terminal Stopping Devices
retain drum m/c, travel increase < 4570mm
|  |  | 2.4.(*) | Vertical Clearances & Runbys for Cars & Cwts
If decrease in rise is at lowest end then;
2.2.4 Access to Pits
2.2.5 Illumination of Pits
2.2.6 Stop Switches
| 8.7.2.17.2 | Increase in Rated Speed |  |  | Major | -
| 8.7.2.17.2(a) | Increase in Rated Speed on a Winding Drum machine |  |  | Major | -
Increase in Rated Speed of a winding drum m/c prohibited
|  |  | 8.7.2.17.2(c) | except as permitted 8.7.2.17.2(c)
| 8.7.2.17.2(b) | Increase in Rated Speed except as per 8.7.2.17.2(c) |  |  | Major | -
|  |  | 2.4.2 | Minimum Bottom Runby for Counterweighted Elevators
|  |  | 2.4.3 | Minimum Bottom Runby for Uncounterweighted Elevators
|  |  | 2.4.4 | Maximum Bottom Runby
|  |  | 2.4.5 | Counterweight Runby Data Plate
|  |  | 2.4.6 | Maximum Upward Movement of the Car
|  |  | 2.4.7 | Top of Car Clearances
|  |  | 2.4.8 | Top of Counterweight Clearances
|  |  | 2.4.9 | Equipment on Top of Car Not Permitted to Strike O/H
|  |  | 2.5. | Horizontal Car and Counterweight Clearances
Car doors or gates shall be provided at all car entrances
|  |  | 2.14. | New doors/gates to: Car: Enclosure, Doors, Gates, Illumination
|  |  | 2.16. | Capacity & Loading
|  |  | 2.17. | Car & Cwt Safeties
|  |  | 2.18.(*) | Speed Governors
|  |  | 2.19. | Ascending Car Overspeed & Unintended Car Movement Protection
|  |  | 2.20. | Suspension Ropes & Connections
|  |  | 2.21.4.2 | Comp Rope Tie Down (if speed > 3.5 m/s)
|  |  | 2.22.(*) | Buffers & Bumpers
|  |  | 2.24. | Driving Machines & Sheaves
|  |  | 2.25. | Terminal Stopping Devices
|  |  | 2.26.(*) | Operating Devices and Control Equipment
| 8.7.2.17.2(c) | Increase in Rated Speed less than 10% & less than 0.20m/s |  |  | Major | -
new spd <.75 for type A safeties
new spd <1 w/spring buffer, 2.18.2.1&.2
|  |  | 2.18.2.1 | Car speed governors
|  |  | 2.18.2.2 | counterweight speed governors
|  |  | 8.7.2.27.3 | Change in Power Supply
| 8.7.2.17.3 | Decrease in Rated Speed |  |  | Major | -
|  |  | 2.4. | Vertical Clearances & Runbys for Cars & Cwts
|  |  | 2.18.2 | Tripping Speeds for Speed Governors
|  |  | 2.16. | Capacity & Loading
|  |  | 2.16.3(*) | Capacity and Data Plates
|  |  | 2.26.4.1 | Electrical Equipment and Wiring
|  |  | 2.26.4.2 | Drive Machine Controllers for Stopping/Starting/Controlling
|  |  | 2.26.4.3 | Positively Opened Contacts
| 8.7.2.18 | Car and Counterweight Safeties |  |  | Major | Major | òSee Below ò
| 8.7.2.18.1 | New Car Safeties |  |  | - | Major | mrr | Minor A
|  |  | 2.17. | Car & Cwt Safeties
|  |  | 2.18. | Speed Governors
|  |  | 2.23. | Car & Cwt Guides Rails, Guide Rail Support, Fastenings
|  |  | 8.7.2.19 | Speed Governors and Governor Ropes
| 8.7.2.18.2 | New Cwt Safeties |  |  | - | Major | mrr | Minor A
|  |  | 2.17. | Car & Cwt Safeties
|  |  | 2.18. | Speed Governors
|  |  | 2.23. | Car & Cwt Guides Rails, Guide Rail Support, Fastenings
|  |  | 8.7.2.19 | Speed Governors and Governor Ropes
| 8.7.2.18.3 | Existing Car Safeties |  |  | Major | - | mrr | Minor A
|  |  | 2.17.(*) | Car & Cwt Safeties
|  |  | 2.18. | Speed Governors
|  |  | 2.23. | Car & Cwt Guides Rails, Guide Rail Support, Fastenings
|  |  | 8.7.2.19 | Speed Governors and Governor Ropes
| 8.7.2.18.3 | Existing Cwt Safeties |  |  | Major | - | mrr | Minor A
|  |  | 2.17. | Car & Cwt Safeties
|  |  | 2.18. | Speed Governors
|  |  | 2.23. | Car & Cwt Guides Rails, Guide Rail Support, Fastenings
|  |  | 8.7.2.19 | Speed Governors and Governor Ropes
| 8.7.2.19 | Speed Governors and Governor Ropes |  |  | Major | Major | òSee Below ò
| 8.7.2.19 |  | 2.18. | Speed Governors |  |  | mrr | Minor A
see
8.6.3.6
| 8.7.2.19 |  | 2.17.15 | Governor Rope Releasing Carriers |  |  | mrr | mrr
see 8.6.3.9
| 8.7.2.19 |  | Governor Ropes of different material or Construction to: |  |  |  | - | Minor B
2.18.6 Design Gov'r Rope Retarding Means for Type B Safeties
2.18.7 Traction between Speed Governor Rope & Sheave
|  |  | & testing to | 2.17.3 Function and Stopping Distances of Safeties
| 8.7.2.20 | Ascending Car Overspeed and Unintended Car Movement Protection (ACO & UCM) |  |  | Minor A | Major | mrr | Minor A
|  |  | 2.19. | Ascending Car Overspd & Unintended Car Movement Protection
| CAD 8.7.2.20«1 | « | If Elevators Controllers are pre-B44-00 & have ACO & UCM |  | Minor A | - | mrr | Minor A
|  |  | 2.19. | ACO & UCM Protection, Except that;
detection means to B44-M90 or the code at time of install
|  |  | 8.9. | Code Data tag to reflect code at time of install
| CAD 8.7.2.20«2 | « | If Elevators Controllers are pre-B44-00 & have ACO ONLY |  | Minor A | - | mrr | Minor A
|  |  | 2.19.1 | ACO Protection Only, Except that;
|  |  | 2.19.3 | Emergency Brake and
detection means to B44-M90 or the code at time of install
|  |  | 2.19.4 | Emergency Brake Supports
|  |  | 8.9. | Code Data tag to reflect code at time of install
| CAD 8.7.2.20«3 | « | Voluntary Addition of Both ACO and UCM where previously not provided |  |  | Minor A
|  |  | 2.19. | ACO & UCM Protection Except that;
detection means to B44-M90 code or later
|  |  | 2.7. | Machinery Spaces, Machine Rooms Control Spaces & Control Rooms
as applicable to the equipment installation
|  |  | 8.9. | Code Data tag to reflect code edition used for the alteration
| 8.7.2.21 | Suspension Ropes and Their Connections |  |  | ò See Below ò
| 8.7.2.21.1 | Change in Number of, or Diameter of Ropes |  |  | Major | -
|  |  | 2.20. | Suspension Ropes & Connections
PEO to certify existing sheaves w/different ropes are satisfactory
| 8.7.2.21.1 | Change in Material / Grade of Ropes |  |  | Minor A | -
|  |  | 2.20. | Suspension Ropes & Connections
PEO to certify existing sheaves w/different ropes are satisfactory
| 8.7.2.21.2 | Addition of Rope Equalizers |  |  | Minor B | Minor B | See 8.6.3.2
|  |  | 2.20.5 | Suspension Rope Equalizers
| 8.7.2.21.3 | Addition of Auxiliary Rope-Fastening Devices |  |  | Major | Major
|  |  | 2.20. | Suspension Ropes & Connections
| 8.7.2.21.4 (a) | Change in Type of Suspension Means |  |  | Major | Major
|  |  | 2.20.8.1 | Protection Against Traction Loss
|  |  | 2.20.8.2 | Broken Suspension Member
|  |  | 2.20.8.3 | Suspension-Member Residual Strength
|  |  | 2.20.11 | Suspension-Member Test
| 8.7.2.21.4 (b) | Traction Loss Detection |  |  | Minor A | Minor A
|  |  | 2.20.8.1 | Protection Against Traction Loss
| 8.7.2.21.4 (c) | Broken Suspension Means Detection |  |  | Minor A | Minor A
|  |  | 2.20.8.2 | Broken Suspension Member
| 8.7.2.22 | Counterweights |  |  | Minor A | -
| 8.7.2.22.1 |  | Alteration to any part of a cwt except guiding members
|  |  | 2.21. | Counterweights
|  |  | 8.7.2.22.2 | Rod Type Counterweights
|  |  | 8.7.2.3 | Location and Guarding of Counterweights
| 8.7.2.22.2 |  | Rod Type Cwt - can retain if:
Minimum of 2 suspension and 2 tie rods
Suspension rods:
|  |  | 2.21.2.1 | Material - Cwt Frames & Rods
|  |  | 2.21.2.3 | Factor of Safety
Tie Rods:
|  |  | 2.21.1.2 | Retention of Weight Sections
| 8.7.2.22.3 |  | Roller or similar guide shoes added |  | mrr |  | mrr
safety jaws cannot touch rails if not activated
| 8.7.2.23 | Car and Counterweight Buffers and Bumpers |  |  | Major | - | mrr | Minor B
|  |  | 2.22.(*) | Buffers & Bumpers
| 8.7.2.24 | Guide Rails, Supports, and Fastenings (alteration to, or stress increase >5%) |  |  | Major | -
|  |  | 2.23. | Car & Cwt Guides Rails, Guide Rail Support, Fastenings
| 8.7.2.25 | Driving Machines and Sheaves |  |  | ò See Below ò
| 8.7.2.25.1 | Alter / Replace |  | Driving Machines & Sheaves | Major | Major | Major
| 8.7.2.25.1(a) |  |  | Driving Machine Installed as part of an alteration | Major | -
|  |  | 2.7.2 | Maintenance Path and Clearance
to extent existing installation permits
|  |  | 2.9. | Machinery & Sheave Beams, Supports, Foundation
|  |  | 2.10.1 | Guarding of Equipment
|  |  | 2.19. | Ascending Car Overspeed & Unintended Car Movement Protection
|  |  | 8.7.2.20 | ACO & UCM Protection
|  | CAD | 8.7.2.20«1 | Pre B44-00 ACO & UCM Protection
|  | CAD | 8.7.2.20«2 | Pre B44-00 ACO Only Protection
|  | CAD | 8.7.2.20«3 | Addition ACO/UCM if not required by other alteration scope
|  |  | 2.20. | Suspension Ropes & Connections
|  |  | 2.24. | Driving Machines & Sheaves
|  |  | 2.26.8 | Release and Application of Driving-Machine Brakes
| 8.7.2.25.1(b) | Alter / Replace |  | Driving Machine Components - affected component complies w/ | Major
|  |  | 2.24.2 | Sheaves and Drums |  |  | mrr | Major
|  |  | 2.24.3 | Factor of Safety for Driving Machines and Sheaves
|  |  | 2.24.4 | Fasteners Transmitting Load
|  |  | 2.24.5 | Shafts Fillets and Keys
|  |  | 2.24.6 | Cast-Iron Worms and Worm Gears
|  |  | 2.24.7 | Friction Gearing and Clutches
|  |  | 2.24.8 | Braking Systems & Driving Machine Brakes |  |  | mrr | Major
|  |  | 2.24.9 | Indirect-Driving Machines
|  |  | 2.26.8 | Release and Application of Driving-Machine Brakes
| 8.7.2.25.1(c) | Change of |  | Driving Machine Sheave | Major | - | mrr | Major
|  |  | 2.24.2 | Sheaves and Drums
|  |  | 2.24.3 | Factor of Safety for Driving Machines and Sheaves
|  |  | 2.24.4 | Fasteners Transmitting Load
|  |  | 2.20. | Suspension Ropes & Connections
| 8.7.2.25.2 | Change in Location of Driving Machine |  |  | Major | -
| 8.7.2.25.2(a) | Change in Location of Driving Machine w/ no change in Rise |  |  | Major | -
|  |  | 2.7.2 | Maintenance Path and Clearance
|  |  | 2.9. | Machinery & Sheave Beams, Supports, Foundation
|  |  | 2.10.1 | Guarding of Equipment
|  |  | 2.24.2.3 | Traction
| 8.7.2.25.2(b) | Change in Location of Driving Machine w/ change in Rise |  |  | Major | -
|  |  | Part 2 (*) | Electric Elevators (entire installation to meet Part 2), except
2.5 Horizontal Car and Counterweight Clearances
2.11 Protection of Hoistway Openings
2.4 Vertical Clearances and Runbys for Cars & Cwts
|  |  | 8.7.2.5 | see also
|  |  | 8.7.2.10 | see also
| CAD 8.7.2.25«1 | « Replacement of worm and/or gear (specify make) |  |  | - | - | mrr | Minor A
|  |  | 2.24 | specify compliance to the applicable requirements
Addition of Machine Guarding - see CAD 8.7.2.7«1
| 8.7.2.26 | Terminal-Stopping Devices |  |  | Minor B | Minor B
|  |  | 2.25. | Terminal Stopping Devices
| 8.7.2.27 | Operating Devices and Control Equipment |  |  | ò See Below ò
| 8.7.2.27.1 | Top-of-Car Operating Devices |  |  | Minor A | Minor A | mrr | Minor A
|  |  | 2.26.1.4 | Inspection Operation
| CAD 8.7.2.27«1 | Alteration / Addition of any type of inspection operation |  |  | Minor A | Minor A
|  |  | 2.26.1.4 | Inspection Operation
| CAD 8.7.2.27«2 | « | Addition of Top-of-Car Operating Device (see CAD 3.8.3) |  | - | Minor A
|  |  | 2.26.1.4 | Inspection Operation
8.7.2.15«1,«2
| 8.7.2.27.2 | Car-Leveling or Truck-Zoning Devices |  |  | Minor A | Minor A
|  |  | 2.26.1.6 | Operation in Leveling or Truck Zone
| CAD 8.7.2.27«3 | « Door By-Pass Switches |  |  | Minor A | Minor A
|  |  | 2.26.1.5 | System to Prevent Auto Operation w/faulty Door Contacts
| CAD 8.7.2.27«4 | « Door Monitoring System |  |  | Minor A | Minor A
|  |  | 2.26.5 | System to Prevent Auto Operation w/faulty Door Contacts
| 8.7.2.27.3 | Change in Power Supply |  |  | Major | -
(a) voltage, frequency or # of phases or
(b) AC to DC , DC to AC or
(c) combination of DC & AC, then
electrical to:
|  |  | 2.26.1.1 | Types of Operation
|  |  | 2.26.1.2 | For Car-Switch Operation Elevators
|  |  | 2.26.1.3 | Add'l Operating Devices for Elevators carrying 1pc. load > than Rated
|  |  | 2.26.1.4 | Inspection Operation
|  |  | 2.26.1.6 | Operation in Leveling or Truck Zone
|  |  | 2.26.2 | Electrical Protective Devices
|  |  | 2.26.6 | Phase Protection of Motors
|  |  | 2.26.7 | Installation of Capacitors/Devices Making EPD's Ineffective
|  |  | 2.26.9 | Control & Operating Circuits
|  |  | 2.26.10 | Absorption of Regenerated Power
new / modified equipment and wiring to:
|  |  | 2.26.4.1 | Electrical Equipment and Wiring
|  |  | 2.26.4.2 | Drive Machine Controllers for Stopping/Starting/Controlling
|  |  | 2.26.4.3 | Positively Opened Contacts
brakes to:
|  |  | 2.24.8 | Braking Systems & Driving Machine Brakes
|  |  | 2.26.8 | Release and Application of Driving-Machine Brakes
winding drum to:
|  |  | 2.25.3.5 | Additional Req'mts for Winding Drum Machines
see 8.7.2.17.2(b) Increase in Rated Speed
| 8.7.2.27.4 | Controllers
| 8.7.2.27.4(a) | Install / Replace |  | Motion or Operation Controller (no change in method) | Major | - | Major
|  |  | 2.25. | Terminal Stopping Devices
|  |  | 2.26.1.4 | Inspection Operation
|  |  | 2.26.1.5 | Inspection Operation with Open Door Circuits
|  |  | 2.26.1.6 | Operation in Leveling or Truck Zone
|  |  | 2.26.2 | Electrical Protective Devices
|  |  | 2.26.3 | Contactor and Relays for Use in Critical Operating Circuits
|  |  | 2.26.4 | Electrical Equipment and Wiring
|  |  | 2.26.5 | System to Monitor & Prevent Automatic Operation w/ Faulty Door Contacts
|  |  | 2.26.6 | Phase Protection of Motors
|  |  | 2.26.7 | Installation of Capacitors/Devices Making EPD's Ineffective
|  |  | 2.26.8 | Release and Application of Driving-Machine Brakes
|  |  | 2.26.9 | Control & Operating Circuits
|  |  | 2.26.11 | Car Platform to Hoistway Door Sills Vertical Distance
levelling accuracy to 13mm (0.5 in.)
|  |  | 2.29. | Identification of Equipment and Floors
|  | « | 2.7.9.2 | Temperature and Humidity
|  |  | 2.27.2 | Emergency or Standby Power systems
If FEO previously present or required by OBC;
|  |  | 2.27.3 | Firefighters' Emergency Operation - Automatic Elevators
2.27.3.1 Phase 1 Recall Operation
2.27.3.2 Phase 1 Recall Operation by FAID's
CAD 2.27.3.2.2
2.27.3.3 Phase 2 Emergency In-Car Operation
2.27.3.4 Interruption of Power
2.27.3.5 Multicompartment Elevators
see 8.7.1.2 safety levels shall not be diminished
|  |  | 2.27.4 | FEO: Non Automatic Elevators
|  |  | 2.27.5 | FEO: Automatic Elevators with Designated-Attendant Operation
|  |  | 2.27.6 | FEO: Inspection Operation
|  |  | 2.27.7 | FEO: Operating Procedures
|  |  | 2.27.8 | Switch Keys
|  |  | 2.27.9 | Elevator Corridor Call Station Pictograph
If FEO NOT previously present or required by OBC;
CAD 2.27.3.2.2
2.27.3.1 Provide Phase 1 Manual Recall Operation Only
| CAD 8.7.2.27«5 | Relocation of |  | Elevator Controller (if control wiring disconnected - reconnected) | Major
|  |  | 2.8.2 | Electrical Equipment and Wiring
Electrical testing to verify functionality of rewired equipment
| 8.7.2.27.4(b) | Installation of |  | Door Controller | Minor A | - | Minor B
|  |  | 2.26.4.1 | Electrical Equipment and Wiring
|  |  | 2.26.4.2 | Drive Machine Controllers for Stopping/Starting/Controlling
| 8.7.2.27.4(c) | Installation of |  | Controller for Emergency or Standby Power | Minor A | Minor A | Minor B
|  |  | 2.26.4.1 | Electrical Equipment and Wiring
|  |  | 2.26.4.2 | Drive Machine Controllers for Stopping/Starting/Controlling
| 8.7.2.27.4(c) | Installation of |  | Controller for FEO Operation | Minor A | Minor A | Minor B
|  |  | 2.26.4.1 | Electrical Equipment and Wiring
|  |  | 2.26.4.2 | Drive Machine Controllers for Stopping/Starting/Controlling
| 8.7.2.27.5 | Change in Type of Motion Control - AC, VVVF, DC, SCR |  |  | Major | -
|  |  | 2.11.1(*) | Entrances and Emergency Doors Required
|  |  | 2.11.2 | Types of Entrances
|  |  | 2.11.3 | Closing of Hoistway Doors
|  |  | 2.11.4 | Location of Horizontally Sliding or Swinging H/W Doors
|  |  | 2.11.5 | Projection of Entrances & Equip. Beyond Land'g Sills
|  |  | 2.11.6(*) | Opening of Hoistway Doors
|  |  | 2.11.8 | Weights for Closing or Balancing Doors
|  |  | 2.11.9 | Hoistway Door Locking Devices & Power Operation
|  |  | 2.11.11.8(*) | Hoistway Door Safety Retainers
|  |  | 2.11.12.8 | Pull Straps
|  |  | 2.12.(*) | H/W-Door Locking Devices, Elec. Contacts, H/W Access
2.12.5 Restricted Opening of Hoistway or Car Doors
2.12.6 Hoistway Door Unlocking Devices
2.12.7 Hoistway Access Switches
|  |  | 2.13. | Power Operation of H/W Doors and Car Doors
|  |  | 2.14.(*) | Car: Enclosure, Doors, Gates, Illumination
2.14.1.7 car top railing
|  |  | 2.16.8(*) | Capacity & Loading
|  |  | 2.17.(*) | Car & Cwt Safeties
|  |  | 2.18.(*) | Speed Governors
|  |  | 2.19. | Ascending Car Overspeed & Unintended Car Movement Protection
|  |  | 8.7.2.20 | ACO & UCM Protection
|  | CAD | 8.7.2.20«1 | Pre B44-00 ACO & UCM Protection
|  | CAD | 8.7.2.20«2 | Pre B44-00 ACO Only Protection
|  | CAD | 8.7.2.20«3 | Addition ACO/UCM if not required by other alteration scope
|  |  | 2.25. | Terminal Stopping Devices
|  |  | 2.26.(*) | Operating Devices and Control Equipment
|  |  | 2.29. | Identification of Equipment and Floors
|  | « | 2.7.9.2 | Temperature and Humidity
If FEO previously present or required by OBC;
|  |  | 2.27. | Emergency Operation and Signalling Devices
2.27.1 Car Emergency Signalling Devices
2.27.2 Emergency or Standby Power Systems
2.27.3 Firefighters' Emergency Operation: Automatic Elevators
2.27.3.1 Phase 1 Recall Operation
2.27.3.2 Phase 1 Recall Operation by FAID's
CAD 2.27.3.2.2
2.27.3.3 Phase 2 Emergency In-Car Operation
2.27.3.4 Interruption of Power
2.27.3.5 Multicompartment Elevators
see 8.7.1.2 safety levels shall not be diminished
2.27.4 FEO: Non Automatic Elevators
2.27.5 FEO: Automatic Elevators with Designated-Attendant Operation
2.27.6 FEO: Inspection Operation
2.27.7 FEO: Operating Procedures
2.27.8 Switch Keys
If FEO NOT previously present or required by OBC;
CAD 2.27.3.2.2
2.27.3.1 Provide Phase 1 Manual Recall Operation Only
| 8.7.2.27.6 | Change in Type of Operation Control - CPPB, AUTOMATIC |  |  | Major | -
|  |  | 2.11.1 | Entrances and Emergency Doors Required
|  |  | 2.11.2 | Types of Entrances
|  |  | 2.11.3 | Closing of Hoistway Doors
|  |  | 2.11.4 | Location of Horizontally Sliding or Swinging H/W Doors
|  |  | 2.11.5 | Projection of Entrances & Equip. Beyond Land'g Sills
|  |  | 2.11.6 | Opening of Hoistway Doors
|  |  | 2.11.7 | Glass in Hoistway Doors
|  |  | 2.11.8 | Weights for Closing or Balancing Doors
|  |  | 2.11.9 | Hoistway Door Locking Devices & Power Operation
|  |  | 2.11.10 | Landing Sill: Guards, Illumination, hinged sills, Tracks
|  |  | 2.11.11 | Entrances, Horizontal Slide Type
|  |  | 2.11.12 | Entrances, Vertical Slide Type
|  |  | 2.11.13 | Entrances, Swing Type
|  |  | 2.12. | H/W-Door Locking Devices, Elec. Contacts, H/W Access
|  |  | 2.13. | Power Operation of H/W Doors and Car Doors
|  |  | 2.14.(*) | Car: Enclosure, Doors, Gates, Illumination
|  |  | 2.16. | Capacity & Loading
|  |  | 2.17. | Car & Cwt Safeties
|  |  | 2.18.(*) | Speed Governors
|  |  | 2.25. | Terminal Stopping Devices
|  |  | 2.26.(*) | Operating Devices and Control Equipment
|  |  | 2.29. | Identification of Equipment and Floors
|  | « | 2.7.9.2 | Temperature and Humidity
|  |  | 2.27. | Emergency Operation & Signaling Devices
2.27.1 Car Emergency Signalling Devices
2.27.2 Emergency or Standby Power Systems
2.27.3 FEO: Automatic Elevators
CAD 2.27.3.2.2
2.27.4 FEO: Non-Automatic Elevators
2.27.5 FEO: Automatic Elevators w/Attendant
2.27.6 FEO: Inspection Operation
2.27.7 FEO: Operating Procedures
2.27.8 Switch Keys
2.27.9 Elevator Corridor Call Station Pictograph if reqd by OBC
| CAD 8.7.2.27«6 | « Addition of Wander Patient Feature - Change in Operation Control |  |  | Minor B | Minor B
|  |  | 2.13.5.3 | - door time out
|  |  | 2.27.3.1.6(l) | - shall not prevent PHI
| CAD 8.7.2.27«7 | « Addition of Restricted Access - Security / Floor Lock Out |  |  | Minor B | Minor B
|  |  | OBC-3.2.6.5(4) | - shall not prevent floor access when on FEO
D.O. Button Remain Operative Under non FEO Conditions, Door Closed When not in Use
|  |  | 2.27.3.3.1(i) | - permit travel to all landings when on PH II
|  |  | 2.11.6.2 | Cannot Lock Out Top& Btm, Designated & Alternate or All Landings in Phase II
| CAD 8.7.2.27«8 | « Addition of Destination Dispatch |  |  |  | Minor B
|  |  | 8.7.2.8 | Electrical Equipment, Wiring, Pipes, and Ducts in H/W's &M/C Rooms
FEO operation to 8.7.2.28 or code at time of installation or alteration
| 8.7.2.27.7 | Removal of emergency stop switch on passenger elevators |  |  | Minor B | -
remove all related markings / engravings & provide an in-car stop switch to:
|  |  | 2.26.2.21 | In-car stop switch
|  | « | 2.26.4.3 | Positively Opened Contacts
|  | « | 2.26.9.3 | Single failure does not render In-Car Stop Sw ineffective
| 8.7.2.27.8 | Electrical Protective Devices |  |  | ò See Below ò
| 8.7.2.27.8 | Alteration or Addition of an Electrical Protective Device |  |  | Major | Major | mrr | Major
if device meets 2.26.4.3.2 (PES)
|  |  | 2.26.2 | Electrical Protective Devices - for specified device
| 8.7.2.27.8 | Alteration or Addition of an Electrical Protective Device |  |  | - | Minor A | mrr
if device meets 2.26.4.3.1
|  |  | 2.26.2 | Electrical Protective Devices - for specified device
| 8.7.2.28 | Emergency Operation and Signaling Devices |  |  | ò See Below ò
| 8.7.2.28 | Car Emergency Signaling Devices |  |  | Minor B | Minor B | mrr
|  |  | 2.27.1 | Car Emergency Signaling Devices
| 8.7.2.28 | Emergency or Standby Power |  |  | Minor B | Minor A
|  |  | 2.27.2 | Emergency Or Standby Power systems
| 8.7.2.28 | Firefighter's Emergency Operation |  |  | Minor B | Minor A
|  |  | 2.27.3 | FEO: Automatic Elevators
|  |  | 2.27.4 | FEO: Non-Automatic Elevators
|  |  | 2.27.5 | FEO: Automatic Elevators w/Attendant
|  |  | 2.27.6 | FEO: Inspection Operation
|  |  | 2.27.7 | FEO: Operating Procedures
|  |  | 2.27.8 | Switch Keys
| 8.7.2.28 | Addition of Elevator to a Group - all elevators to meet: |  |  | - | Minor A
|  |  | 2.27. | Emergency Operation & Signaling Devices
2.27.1 Car Emergency Signalling Devices
2.27.2 Emergency or Standby Power Systems
2.27.3 FEO: Automatic Elevators
CAD 2.27.3.2.2
2.27.4 FEO: Non-Automatic Elevators
2.27.5 FEO: Automatic Elevators w/Attendant
2.27.6 FEO: Inspection Operation
2.27.7 FEO: Operating Procedures
2.27.8 Switch Keys
2.27.9 Elevator Corridor Call Station Pictograph if reqd by OBC
| CAD 8.7.2.28«1 | « Emerg. Recall Upgrade - from Manual to Automatic & matching code at time of install |  |  | Minor B
conformance to auto recall based on F.S. at time of install
| CAD 8.7.2.28«2 | « Emerg. Recall Upgrade to comply with a Fire Code Retrofit Order |  |  | Minor B | Minor A
2.27.3 FEO: Automatic Elevators
|  |  | CAD 3.20 | Fire Code Retrofits

## 8.7.3 Hyd
0 | 1 | 2a | 2b | 2c | 3 | 4 | 5 | 6
Conforms to B44 Mark with 'X' | B44-10 Reference Number | Alteration Checklist for Director's Guideline 251-11-r2 Scope of Alteration - B44 - 2010 as amended by CAD 261/13-r1 Part, Section or Requirement |  |  | Type of Alteration Work
[5 empty] | Alteration |  | Replacement with
[5 empty] | Modification Change | Addition | Same | Different Make/Model
|  | Job Reference: |  |  | Type of Submission Required
| 8.7.1.2 | Alterations not specifically covered in 8.7
|  |  | 1.2 | Level of safety shall not be diminished
| 8.7.1.4 | Welding
|  |  | 8.8 | Welding
|  |  | 8.7.1.5 | Design / Weld Engineer
| 8.7.1.7 | Repairs and Replacements
|  |  | 8.6.2 | for repairs
|  |  | 8.6.3 | for replacements
| 8.7.3.« | Alteration - Hydraulic to Electric Elevator
| 8.7.3.«1 | Where a hydraulic elevator operated in an existing hoistway and a new electric elevator will be installed in its place, the following conditions will apply: |  |  | New
|  | « | Part 2 | Electric Elevators, except:
|  | « |  | Existing building conditions not in full conformance with current requirements may be retained. Identify each deviation in the submission (box 4000) ie.
- pit depth
- no pit drain
|  | « |  | A New Installation Number will be issued
|  | « | 2.15.9 | Apron plate length per 2.15.9 or
- collapsible / telescopic / folding design utilized
| 8.7.1.2 | Alterations not specifically covered in 8.7
|  |  | 1.2 | Level of safety shall not be diminished
| 8.7.1.4 | Welding
|  |  | 8.8 | Welding
|  |  | 8.7.1.5 | Design / Weld Engineer
| 8.7.1.7 | Repairs and Replacements
|  |  | 8.6.2 | for repairs
|  |  | 8.6.3 | for replacements
| 8.7.3 | Alterations to Hydraulic Elevators
| 8.7.3.1 | Hoistway Enclosures |  |  | see 8.7.2.1
| 8.7.2.1 | Hoistway Enclosures |  |  | Major | Major
| 8.7.2.1.1 | Hoistway Enclosure Walls |  |  | Major | Major
|  |  | 2.1.1 | Hoistway Enclosures
|  |  | 2.1.5 | Windows and Skylights
|  |  | 2.1.6 | Projections, Recesses, and Setbacks in H/W
|  |  | 2.5. | Horizontal Car and Counterweight Clearances
|  |  | 2.7.3.4.6 | Access Doors and Openings
|  | « | 2.7.3.4.7 | Access Doors and Openings
|  |  | 2.8. | Equipment in Hoistways,Machinery Spaces, Machine Rooms, Control Spaces, and Control Rooms
|  |  | 8.7.2.10 | Entrances and Hoistway Openings (if change includes an entrance)
|  |  | 2.11.1 | Entrances and Emergency Doors Required (if blind H/W)
| 8.7.2.1.2 | Addition of Elevator to Existing Hoistway |  |  | - | New
|  |  | B44-2010 | New Installation
|  |  | 2.5. | Horizontal Car and Counterweight Clearances
| 8.7.2.1.3 | Construction at Top of Hoistway |  |  | Major | Major
|  |  | 2.1.2.1 | Construction at Top of the Hoistway
|  |  | 2.1.3 | Floor Over Hoistways
|  |  | 8.7.2.4 | Vertical Car & Cwt Clearances & Runbys
| 8.7.2.1.4 | Construction at Bottom of Hoistway |  |  | Major | Major
|  |  | 2.1.2.2 | Construction at Bottom of the Hoistway
|  |  | 2.1.2.3 | Strength of Pit Floor
|  |  | 2.2. | Pits
|  |  | 8.7.2.4 | Vertical Car & Cwt Clearances & Runbys
| 8.7.2.1.5 | Control of Smoke and Hot Gases |  |  | Major | Major
|  |  | 2.1.4 | Control of Smoke and Hot Gases
| 8.7.3.2 | Pits |  |  | see Electric Elevators
| 8.7.2.2 | Pits | see other alterations below for non Major Alterations |  | Major | -
|  |  | 2.2. | Pits
|  |  | 2.1.2.3 | Strength of Pit Floor
|  |  | 8.7.3.4 | Vertical Car & Cwt Clearances & Runbys
| 8.7.2.2 | Pit Drains & Sumps |  |  | Minor B | Minor B
|  |  | 2.2.2. | Pit Drains
| 8.7.2.2 | Pit Guards |  |  | Minor B | Minor A
|  |  | 2.2.3 | Guards Between Adjacent Pits
| 8.7.2.2 | Pit Access |  |  | Minor B | Minor A
|  |  | 2.2.4 | Pit Access
| 8.7.2.2 | Pit Illumination |  |  | Minor B | Minor B
|  |  | 2.2.5 | Illumination of Pits
| 8.7.2.2 | Pit Stop Switches |  |  | Minor B | Minor A
|  |  | 2.2.6 | Stop Switches
| 8.7.2.2 | Pit Depth |  |  | Minor B | Minor A
|  |  | 2.2.7 | Minimum Pit Depths Required
| 8.7.2.2 | Access to Underside of Car |  |  | Minor B | Minor A
|  |  | 2.2.8 | Access to Underside of Car
| 8.7.3.3 | Location and Guarding of Counterweights |  |  | Major | Major
|  |  | 2.3. | Location and Guarding of Counterweights
|  |  | 2.5.1.2 | Between Car & Cwt and Cwt Guard
|  |  | 3.5. | Horizontal car and Counterweight Clearances
| 8.7.3.4 | Vertical Car and Counterweight Clearances and Runbys (no reduction allowed) |  |  | Major | -
|  |  | 3.4. | Bottom and Top Clearances and Runbys for Cars and Cwts
|  |  | 8.7.3.22.1 | Increase or Decrease in Rise
|  |  | 8.7.3.22.2 | Increase in Rated Speed
|  |  | 8.7.3.23.5 | Change in Location of Hydraulic Jack
| 8.7.3.5 | Horizontal Car and Counterweight Clearances (no reduction allowed) |  |  | Major | -
|  |  | 2.5. | Horizontal Car and Counterweight Clearances
|  |  | 8.7.3.22.1 | Increase or Decrease in Rise
|  |  | 8.7.3.22.2 | Increase in Rated Speed
|  |  | 8.7.3.23.5 | Change in Location of Hydraulic Jack
| 8.7.3.6 | Protection of Spaces Below Hoistways |  |  | Minor B | Major
|  |  | 3.6. | Protection of Spaces below Hoistway
| 8.7.3.7 | Machine Rooms and Machinery Spaces |  |  | see 8.7.2.7
| 8.7.2.7 | Machine Rooms and Machinery Spaces |  |  | ò See Below ò
| 8.7.2.7.1 | Enclosures - other than specifics of 8.7.2.7.2 to 8.7.2.7.7
|  |  | 2.7. (& 3.7.) | New - Machinery Spaces, Machine Rooms Control Spaces & Control Rooms | - | Major
|  |  | 2.7. (& 3.7.) | Altered- Machinery Spaces, Machine Rooms Control Spaces & Control Rooms | Minor A | -
|  |  | OESC (C22.1) | Electrical Equipment Clearances | Minor B | -
| 8.7.2.7.2 | Means of Access |  |  | Minor B | -
|  |  | 2.7.3.1 | General Requirements
|  |  | 2.7.3.2 | Access Across Roofs
|  |  | 2.7.3.3 | Means of Access
| 8.7.2.7.3 | Access Doors and Openings |  |  | Minor B | Minor B | mrr
|  |  | 2.7.3.4 | Access Doors and Openings
|  |  | 2.7.3.5 | Stop Switch in O/H M/C Space in the H/W
| 8.7.2.7.4 | Headroom (no reduction) |  |  | Minor B | Minor B
|  |  | 2.7.4 | Headroom in M/C Rooms
| 8.7.2.7.5 | Windows and Skylights |  |  | Minor B | Minor B
2.1.5
| 8.7.2.7.6 | Lighting (no reduction) |  |  | Minor B | Minor A
|  |  | 2.7.9.1 | Lighting
| 8.7.2.7.7 | Ventilation |  |  | Minor B | Minor B
|  |  | 2.7.9.2 | Temperature & Humidity
| CAD 8.7.2.7«1 | Addition of Elevator Equipment Guarding |  |  | Minor A (per m/c rm) |  | mrr | mrr
|  |  | 2.7.2 | Maintenance Path and Clearance
|  |  | 2.7.3.4.2 | Size of doors and openings in cage style enclosures (750x2030)
|  |  | 2.10.1 | Guarding of Equipment
openable/removable only with tools
operating/work instruction for accessing equipment
clearances in front of electrical control equipment (1000mm)
access in front of / space to operate main disconnect (750mm)
Installation by registered contractor
| 8.7.3.8 | Electrical Wiring, Pipes, and Ducts in Hoistways and Machine Rooms |  |  | Minor B | Minor B | mrr | Minor B
|  | Installation of New (electrical equipment, wiring, raceways, cables, pipes, ducts) |  |  | - | Minor B
also installation of Monitoring Equipment, HVAC
|  |  | 2.8. | Equipment in Hoistways and Machine Rooms
CSA Labeling (or equivalent)
OESC, CSA C22.1 as required
|  | Alteration of Existing (electrical equipment, wiring, raceways, cables, pipes, ducts…) |  |  | Minor B | -
|  |  | 2.8. | Equipment in Hoistways and Machine Rooms
| 8.7.3.9 | Machinery and Sheave Beams, Supports and Foundations |  |  | Major | Major
New/Relocated Machinery & Sheave Beams, Supports, Foundation
|  |  | 2.9. | Machinery & Sheave Beams, Supports, Foundation
Building reactions increased by more than 5%
|  |  | 2.9. | Machinery & Sheave Beams, Supports, Foundation
adequacy of building structure verified by P.Eng.
| 8.7.3.10 | Hoistway Entrances and Openings - see 8.7.2.10 |  |  | see 8.7.2.10
| 8.7.2.10 | Entrances and Hoistway Openings |  |  | Major | Major | see below
| 8.7.2.10.1 | General Requirements |  |  | Major | -
| 8.7.2.10.1(a) | General Requirements - All New Entrances |  |  | Major | -
|  |  | 2.11. | Protection of H/W Openings
|  |  | 2.12. | H/W-Door Locking Devices, Elec. Contacts, H/W Access
|  |  | 2.13. | Power Operation of H/W Doors and Car Doors
|  |  | 2.29.2 | Identification of Floors
| 8.7.2.10.1(b) | General Requirements - New Entrances w/Existing Entrances |  |  | - | Major
|  |  | 2.11.2 | Types of Entrances
|  |  | 2.11.3 | Closing of Hoistway Doors
|  |  | 2.11.4 | Location of Horizontally Sliding or Swinging H/W Doors
|  |  | 2.11.5 | Projection of Entrances & Equip. Beyond Land'g Sills
|  |  | 2.11.6 | Opening of Hoistway Doors
|  |  | 2.11.7 | Glass in Hoistway Doors
|  |  | 2.11.8 | Weights for Closing or Balancing Doors
|  |  | 8.7.2.10.5 | Marking of Entrance Assemblies
Entire installation to meet:
|  |  | 2.11.6 | Opening of Hoistway Doors
|  |  | 2.12. | H/W-Door Locking Devices, Elec. Contacts, H/W Access
|  |  | 2.13. | Power Operation of H/W Doors and Car Doors
|  |  | 2.29.2 | Identification of Floors
| 8.7.2.10.1(c) | General Requirements - Alteration to H/W Entrance |  |  | Major | -
|  |  | 2.11.3 | Closing of Hoistway Doors
|  |  | 2.11.5 | Projection of Entrances & Equip. Beyond Land'g Sills
|  |  | 2.11.7 | Glass in Hoistway Doors
|  |  | 2.11.8 | Weights for Closing or Balancing Doors
|  |  | 8.7.2.10.5 | Marking of Entrance Assemblies
Entire installation to meet:
|  |  | 2.12. | H/W-Door Locking Devices, Elec. Contacts, H/W Access
|  |  | 2.13. | Power Operation of H/W Doors and Car Doors
|  |  | 2.29.2 | Identification of Floors
| 8.7.2.10.1(d) | General Requirements - Emergency Doors (added or altered) |  |  | Major | Major
|  |  | 2.11.1 | Entrances and Emergency Doors Required
|  |  | 8.7.2.10.5 | Marking of Entrance Assemblies
| 8.7.2.10.1(e) | General Requirements - Access Openings (installed for cleaning) |  |  | Major | Major
|  |  | 2.11.1.4 | Access Opening for Cleaning of Car & H/W Enclosure
|  |  | 8.7.2.10.5 | Marking of Entrance Assemblies
| 8.7.2.10.2 | Horizontal Slide-Type Entrances - new entrance and components to meet: |  |  | Major | Major | see below
|  |  | 8.7.2.10.1 | Entrances & H/W Openings - General Req'mts |  |  | Major
|  |  | 2.11.11 | Entrances, Horizontal Slide Type
| sills (a) |  | 2.11.10.1 | Landing-Sill Guards | Minor B |  | Minor B
|  |  | 2.11.11.1 | Landing Sills
|  |  | 2.11.11.6 | Bottom Guides
| track (b) |  | 2.11.11.2 | Hanger Tracks, and Track Supports | Minor B |  | Minor B
| frame (c) |  | 2.11.11.3 | Entrance Frames | Minor A |  | Minor A
|  |  | 2.11.11.5.1 | Panel Overlap
|  |  | 2.11.11.5.2 | Panel Gaps Clearances
|  |  | 2.11.11.5.3 | Pockets in Strike Jamb
|  |  | 8.7.2.10.5 | Marking of Entrance Assemblies
| hangers (d) |  | 2.11.11.4 | Hangers | Minor B |  | Minor B
| panels (e) |  | 2.11.11.5(*) | Panels | Minor A |  | Minor A
|  |  | 2.11.11.6 | Bottom Guides
|  |  | 2.11.11.7 | Multipanel Entrances
|  |  | 8.7.2.10.5 | Marking of Entrance Assemblies
| retainers (f) |  | 2.11.11.8 | Hoistway Door Safety Retainers | Minor B |  | Minor B
| 8.7.2.10.3 | Vertical-Slide-Type Entrances - new entrance and components to meet: |  |  | Major | Major | see below
|  |  | 8.7.2.10.1 | Entrances & H/W Openings - General Req'mts |  |  | Major
|  |  | 2.11.12 | Entrances, Vertical Slide Type
| sills (a) |  | 2.11.10.3 | Hinged Hoistway Landing Sills | Minor B |  | Minor B
|  |  | 2.11.12.1 | Landing Sills
| frames (b) |  | 2.11.12.2 | Entrances Frames | Minor B |  | Minor B
|  |  | 8.7.2.10.5 | Marking of Entrance Assemblies
| rails (c) |  | 2.11.12.3 | Rails | mrr |  | mrr
| panels (d) |  | 2.11.12.4 | Panels | Minor A |  | Minor A
|  |  | 2.11.12.3 | Rails
|  |  | 2.11.12.5 | Guides
|  |  | 2.11.12.6 | Counterweighting or Counterbalancing
|  |  | 2.11.12.8 | Pull Straps
|  |  | 8.7.2.10.5 | Marking of Entrance Assemblies
| guides (e) |  | 2.11.12.5 | Guides | mrr |  | mrr
| sill guard (f) |  | 2.11.12.7 | Sill Guards
| straps (g) |  | 2.11.12.8 | Pull Straps
| 8.7.2.10.4 | Swing-Type Entrances - new entrance and components to meet: |  |  | Major | Major | see below
|  |  | 8.7.2.10.1 | Entrances & H/W Openings - General Req'mts |  |  | Major
|  |  | 2.11.13 | Entrances, Swing Type
| sills (a) |  | 2.11.10.1 | Landing-Sill Guards | Minor B |  | Minor B
|  |  | 2.11.10.3 | Hinged Hoistway Landing Sills
|  |  | 2.11.13.1 | Landing Sills
| frames (b) |  | 2.11.13.2 | Entrance Frames | Minor B |  | Minor B
|  |  | 2.11.13.4 | Hinges
|  |  | 8.7.2.10.5 | Marking of Entrance Assemblies
| panels (c) |  | 2.11.13.3 | Panels | Minor B |  | Minor B
|  |  | 2.11.13.4 | Hinges
|  |  | 2.11.13.5 | Marking
|  |  | 8.7.2.10.5 | Marking of Entrance Assemblies
| hinges (d) |  | 2.11.13.4 | Hinges | mrr |  | mrr
| 8.7.2.10.5 | Marking of Entrance Assemblies (Alteration to an Entrance Door Panel) |  |  | Major | Major
Fire Protection Rating not less then existing entrance
|  |  | 8.7.2.10.5(a) | NBCC requirements
| CAD 8.7.2.10«1 | « Removing Service To a Floor |  |  | Minor B
Bolt entrances shut
Remove Interlock From Safety String
Remove COP Floor Button
|  |  | 2.11.6.2 | Cannot Lock Out Top/Btm, Designated/Alternate, All Landing in Phase II
|  |  | 2.12.7 | H/W Access Switches - if floor was previously the access location
| CAD 8.7.2.10«2 | « Door Safety Retainers |  |  | Minor B | Minor A | mrr | Minor B
|  |  | 2.11.11.8 | Hoistway Door Safety Retainers
| 8.7.3.11 | Hoistway Door-Locking Devices |  |  | See 8.7.2.11
| 8.7.2.11 | Hoistway Door-Locking Devices, Access Switches & Parking Devices |  |  | ò See Below ò
| 8.7.2.11.1 | Interlocks |  |  | - | Major | mrr | Minor B
|  |  | 2.12.1 | General
|  |  | 2.12.2 | Interlocks
|  |  | 2.12.4 | Listing/Certification Locking Devices
|  |  | 2.12.5 | Restricted Opening of H/W or Car Door (n/a for column 5,6) |  |  | n/a
|  |  | 2.12.6 | Hoistway Door Unlocking Devices (n/a for column 5,6) |  |  | n/a
|  |  | 2.12.7 | Hoistway Access Switches (n/a for column 5,6) |  |  | n/a
| 8.7.2.11.2 | Mechanical Locks and Electric Contacts |  |  | - | Major | mrr | Minor B
|  |  | 2.12.1 | General
|  |  | 2.12.3 | H/W Door Combination Mechanical Locks & Contacts
|  |  | 2.12.4 | Listing/Certification Locking Devices
|  |  | 2.12.6 | Hoistway Door Unlocking Devices
| 8.7.2.11.3 | Parking Devices |  |  | Minor A | Minor A
|  |  | 8.7.2.11.3 | requirements specified
| 8.7.2.11.4 | Access switches and Unlocking Devices
| 8.7.2.11.4 (a) | Addition of Unlocking Devices |  |  | - | Minor B | mrr
|  |  | 2.12.6 | Hoistway Door Unlocking Devices
| 8.7.2.11.4 (b) | Addition of Access Switches |  |  | - | Minor A | mrr
|  |  | 2.12.7 | Hoistway Access Switches
|  |  | 2.24.8 | Braking Systems & Driving Machine Brakes
|  |  | 2.26.1.4 | Inspection Operation
| 8.7.2.11.5 | Restricted Opening of H/W or Car Doors of Passenger Elevators (Restrictors) (Altered or Installed) |  |  | Minor B | Minor B | mrr | Minor B
|  |  | 2.12.5 | Restricted Opening of H/W or Car Door
| 8.7.3.12 | Power Operation of Hoistway Doors (Addition / Alteration to Power Open or Close) |  |  | Minor A | Minor A
|  |  | 8.7.2.10.1 | Entrances & H/W Openings - General Req'mts
|  |  | 8.7.2.10.2 | Horizontal Slide-Type Entrances
|  |  | 8.7.2.10.3 | Vertical Slide-Type Entrances
|  |  | 8.7.2.10.5 | Marking of Entrance Assemblies
|  |  | 8.7.3.10 | Hoistway Entrances and Openings
|  | « | 2.13. | Power Operation of Hoistway Doors and Car Doors
| CAD 8.7.2.12«1 | « Replacement of Door Operator |  |  | - | - | mrr | Minor B
|  |  | 2.13. | Power Operation of Hoistway Doors and Car Doors
8.7.2.15«1,«2
| CAD 8.7.2.12«2 | « Replacement of Door Reopening Device |  |  | See 8.7.2.13
| 8.7.2.13 | Door Reopening Device (Safety Edge) (Altered or Added or Replaced) |  |  | Minor B | Minor B | mrr | Minor B
|  |  | 2.13.4 | Closing Limitations for Power Operated HS Doors & Gates |  |  | see
|  |  | 2.13.5 | Reopening Device for Power Operated Car Doors or Gates |  |  | 8.6.3.8
if FEO provided, door opening & closing to PHI &II at time of install
8.7.2.15«1,«2
| 8.7.3.13 | Car Enclosures |  |  | See 8.7.2.14
| 8.7.2.14 | Car Enclosures, Car Doors and Gates, and Car Illumination |  |  | ò See Below ò
| 8.7.2.14.1 | Installation of New Car Enclosure |  |  | Major | -
|  |  | 2.14. | Car: Enclosure, Doors, Gates, Illumination
|  |  | 2.15. | Car Frames & Platforms
|  |  | 2.17 | Car and counterweight safeties
|  |  | 8.7.2.15.1 | Alterations to Car Frames and Platforms
| 8.7.2.14.2 | Alteration to Existing Cars |  |  | Minor A | Minor A
| 8.7.2.14.2(a) | Car Enclosure - Securing of Enclosures |  |  | Minor A | Minor A
|  |  | 2.14.1.2 | Securing of Enclosures
| 8.7.2.14.2(b) | Top Emergency Exit (Altered or Added) |  |  | Minor B | Minor B
|  |  | 2.14.1.5 | Top Emergency Exits
| 8.7.2.14.2(c) | Installation of Glass |  |  | Minor B | Minor B
|  |  | 2.14.1.8 | Glass in Elevator Cars
|  |  | 2.14.1.8.1 | Enclosures include glass
|  |  | 2.14.1.8.2 | Lining of Walls or Ceilings include glass |  |  | mrr
|  |  | 2.14.1.8.3 | Marking of each Glazing Panel
| 8.7.2.14.2(d) | Specific Equipment in Elevator Car |  |  | Minor B | Minor B
|  |  | 2.14.1.9 | Equipment Inside Cars
|  |  | (a) | Handrails
|  |  | (b) | fastening devices for protective linings
|  |  | (c) | ceiling mounted hooks/tracks
|  |  | (d) | picture frames display boards, plaques <38mm protrusion
secured to 2.14.1.2
material to 2.14.2.1
|  |  | (e) | conveyor tracks in freights
|  |  | ( f) | heating or cooling equipment
8.7.2.15«1,«2
| CAD 8.7.2.14«1 | « Car operating station |  |  | Minor B | Minor B | mrr | Minor B
verify inspection operation 'if provided'
verify stop sw
verify switches operate as before (eg. FS, FEO, Access)
8.7.2.15«1,«2
| CAD 8.7.2.14«2 | « video cameras / surveillance equipment / video monitors |  |  | Minor B | Minor B
|  |  | 2.8.2.1 | electrical equipment & wiring
|  |  | 2.14.1.2.3 | securing of enclosure equipment
|  |  | 2.14.2.4 | Headroom in Elevator Cars
8.7.2.15«1,«2
| CAD 8.7.2.14«3 | « other equipment |  |  | Variance
| 8.7.2.14.2(e) | Side Emergency Exits - Secured Shut |  |  | Major | -
| 8.7.2.14.2(f) | Car Ventilation |  |  | Minor B | -
|  |  | 2.14.2.3 | Ventilation
| 8.7.2.14.2(g) | Car Illumination |  |  | Minor B | Minor B
|  |  | 2.14.7 | Illumination of Cars and Lighting Fixtures
| 8.7.2.14.2(h) | Partitions Installed in Elevator Cars |  |  | Major | Major
|  |  | 2.16.1.2 | Use of Partitions for Reducing Inside Net Platform Area
| 8.7.2.14.2(i) | Installation of Car Door or Gate, Installation to meet: |  |  | Major | Major
|  |  | 2.14.4 | Passenger and Freight Car Doors/Gates, General Requirements
|  |  | 2.14.5 | Passenger Car Doors
|  |  | 2.14.6 | Freight Elevator Car Doors and Gates
| 8.7.2.14.4 | Car Enclosure / Car Door or Car Gates |  |  | ò See Below ò
| 8.7.2.14.4 | Alteration to Car Enclosure other than 8.7.2.14.2 - Enclosure Materials
|  |  | 2.14. | Car: Enclosure, Doors, Gates, Illumination
enclosure material flame ratings shall not be diminished
|  |  |  | 2.14.1.7 car top railing - see CAD 8.7.2.14«4 |  | Minor A
|  |  |  | 2.14.7.1.3 auxiliary lighting |  | Minor B
|  |  |  | 2.14.7.1.4 car top light & outlet |  | Minor B
|  |  | « | CAD 8.7.2.15«1 | Minor B |  | Minor B
or
|  |  | « | CAD 8.7.2.15«2 | Minor A |  | Minor A
| 8.7.2.14.4 | Alteration to Car Door or Car Gates other than 8.7.2.14.2 |  |  | Minor A | Minor A
|  |  | 2.14. | Car: Enclosure, Doors, Gates, Illumination
2.14.1.7 car top railing
2.14.7.1.3 auxiliary lighting
2.14.7.1.4 car top light & outlet
| O.Reg.209/01s30 | « Relocation of Elevator License to remote location |  |  | Minor B† | -
| CAD 8.7.2.14«4 | « Car Top Guard Rail |  |  | Minor B | Minor A | - | Minor A
|  | CAD | 8.7.2.14«4(a) | Standard Guardrail (to CAD 8.7.2.14«4(a), 2.14.1.7 & OBC)
or
|  | CAD | 8.7.2.14«4(b) | Foldable Guardrail (to CAD 8.7.2.14«4(b), 2.14.1.7 & OBC)
car top run buttons not enabled until extended
normal operation not enabled until stowed
electrical limits to ensure car top clearance in overhead
minor A submission template
|  |  | 8.7.2.15«1,«2 | car weighed prior to alteration
| 8.7.3.14 | Car Frames and Platforms |  |  | Major | - | Major
|  |  | 3.15. | Car Frames & Platforms
| 8.7.3.15 | Safeties |  | Car or Cwt (plunger gripper see 8.7.3.23.7) | ò See Below ò
| 8.7.3.15.1 | Car Safeties |  |  | - | Major | mrr | Minor A
|  |  | 3.17.1 | Car Safeties
|  |  | 3.23. | Guide Rails, Guide-Rail Supports, and Fastenings
|  |  | 3.28. | Layout Data
| 8.7.3.15.2 | Counterweight Safeties |  |  | - | Major | mrr | Minor A
|  |  | 3.17.2 | Counterweight Safeties
|  |  | 3.23. | Guide Rails, Guide-Rail Supports, and Fastenings
|  |  | 3.28. | Layout Data
| 8.7.3.15.3 | Alteration to existing Car or Counterweight Safeties |  |  | Major | - | mrr | Minor A
|  |  | 3.17(*) | Car and counterweight safeties and plunger gripper
|  |  | 3.23. | Guide Rails, Guide-Rail Supports, and Fastenings
|  |  | 3.28. | Layout Data
| 8.7.3.16 | Governors and Governor Ropes |  |  | See 8.7.2.19
| 8.7.2.19 | Speed Governors and Governor Ropes |  |  | Major | Major | òSee Below ò
| 8.7.2.19 |  | 2.18. | Speed Governors |  |  | mrr | Minor A
see
8.6.3.6
| 8.7.2.19 |  | 2.17.15 | Governor Rope Releasing Carriers |  |  | mrr | mrr
see 8.6.3.9
| 8.7.2.19 |  | Governor Ropes of different material or Construction to: |  |  |  | Minor B | Minor B
2.18.6 Design of Gov'r Rope Retarding Means for Type B Safeties
2.18.7 Traction between Speed Governor Rope & Sheave
|  |  | & testing to | 2.17.3 Function and Stopping Distances of Safeties
| 8.7.3.17 | Change in Type of Service: Passenger to Freight OR Freight to Passenger |  |  | Major | -
|  |  | 2.11.1(*) | Entrances and Emergency Doors Required
|  |  | 2.11.2 | Types of Entrances
|  |  | 2.11.3 | Closing of Hoistway Doors
|  |  | 2.11.5 | Projection of Entrances & Equip. Beyond Land'g Sills
|  |  | 2.11.6 | Opening of Hoistway Doors
|  |  | 2.11.7 | Glass in Hoistway Doors
|  |  | 2.11.8 | Weights for Closing or Balancing Doors
|  |  | 2.12. | H/W-Door Locking Devices, Elec. Contacts, H/W Access
|  |  | 2.13. | Power Operation of H/W Doors and Car Doors
|  |  | 2.22.(*) | Buffers & Bumpers
|  |  | 3.22.2 | Counterweight Buffers
|  |  | 3.14. | Car: Enclosure, Doors, Gates, Illumination
|  |  | 2.14. | Car: Enclosure, Doors, Gates, Illumination
|  |  | 2.14.1.7.1 | car top guard rail to 8.7.2.144
|  |  | 3.15. | Car Frames & Platforms
|  |  | 3.17. | Car and Counterweight Safeties
|  |  | 3.21. | Counterweights
|  |  | 3.23. | Guide Rails, Guide-Rail Supports, and Fastenings
|  |  | 2.18.(*) | Speed Governors
|  |  | 3.16. | Capacity & Loading
|  |  | 3.18. | Hydraulic Jacks
|  |  | 3.19. | Valves, Pressure Piping, and Fittings
|  |  | 3.20. | Ropes and Rope Connections
|  |  | 3.24. | Hydraulic Machines and Tanks
|  |  | 3.25. | Terminal-Stopping Devices
|  |  | 3.26. | Operating Devices and Control Equipment
|  |  | 3.27. | Emergency Operation and Signaling Devices
3.27.1 PHI Emergency Recall Operation After Device Actuation
(a) low oil protection
(b) plunger follower guide protection
(c) auxiliary power lowering
(d) oil tank temperature shutdown
2.27 Emergency Operation & Signaling Devices
2.27.1 Car Emergency Signalling Devices
2.27.2 Emergency or Standby Power Systems
2.27.3 FEO: Automatic Elevators
CAD 2.27.3.2.2
2.27.4 FEO: Non-Automatic Elevators
2.27.5 FEO: Automatic Elevators w/Attendant
2.27.6 FEO: Inspection Operation
2.27.7 FEO: Operating Procedures
2.27.8 Switch Keys
2.27.9 Elevator Corridor Call Station Pictograph if reqd by OBC
| 8.7.3.18 | Change in Class of Loading: [A, B, C1, C2, C3] |  |  | Major | -
|  |  | 2.16.2 | Minimum Rated Load for Freight Elevators
|  |  | 3.16. | Capacity & Loading
| 8.7.3.19 | Carrying of Passengers on Freight Elevators |  |  | Major | -
|  |  | 3.16.4 | 2.16.4 except 2.16.4.3
|  |  | 2.16.4 | Carrying of Passengers on Freight Elevators
|  |  | 2.16.4.1 | not accessible to general public
|  |  | 2.16.4.2 | rated load not less than required by 2.16.1
|  |  | 2.16.4.4 | H/W entrances to 2.12.1.1 & 2.11.2.1 or 2.11.2.2(e)
|  |  | 2.16.4.5 | car doors to 2.14.5 Passenger Car Doors
|  |  | 2.16.4.6 | car enclosure openings to 2.14.2.2 Prohibited Openings
|  |  | 2.16.4.7 | conforms to 2.12.5 Restricted Opening of H/W or Car Door
|  |  | 2.16.4.8 | Fs for suspension ropes to Table 2.20.3
|  |  | 2.16.4.9 | Power Operated vertical doors to 2.16.4.9(a) to (e)
|  |  | « | apron guard to ED CAD or extent pit permits
|  |  | « | 2.16.5 Signs Required in Freight Elevator Cars
| 8.7.3.20 | Increase in Rated Load |  |  | Major | -
|  |  | 2.26.1.4 | Inspection Operation
|  |  | 2.26.1.5 | Inspection Operation with Open Door Circuits
|  |  | 2.26.5 | Monitor & Prevent Automatic Operation w/ Faulty Door Contacts
|  |  | 3.14. | Car: Enclosure, Doors, Gates, Illumination
|  |  | 2.14. | Car: Enclosure, Doors, Gates, Illumination
|  |  | 2.14.1.7.1 | car top guard rail to CAD 8.7.2.144
|  |  | 3.15. | Car Frames & Platforms - «apron guard to ED CAD/as pit permits
|  |  | 3.16. | Capacity & Loading
|  |  | 3.17. | Car and Counterweight Safeties
|  |  | 3.20. | Ropes and Rope Connections
|  |  | 3.21. | Counterweights
|  |  | 3.22. | Buffers and Bumpers
|  |  | 3.23. | Guide Rails, Guide-Rail Supports, and Fastenings
|  |  | 8.7.3.23.4 | Increase in Working Pressure
| 8.7.3.21 | Increase in Deadweight of Car (Car Wt+Rated Load >5%) |  |  | Major | -
|  |  | 3.14. | Car: Enclosure, Doors, Gates, Illumination | n/a
|  |  | 2.14. | Car: Enclosure, Doors, Gates, Illumination
|  |  | 2.14.1.7.1 | car top guard rail to 8.7.2.144
|  |  | 3.15. | Car Frames & Platforms - «apron guard to ED CAD/as pit permits
|  |  | 3.16. | Capacity & Loading
|  |  | 3.17. | Car and Counterweight Safeties
|  |  | 3.20. | Ropes and Rope Connections
|  |  | 3.21. | Counterweights
|  |  | 3.22. | Buffers and Bumpers
|  |  | 3.23. | Guide Rails, Guide-Rail Supports, and Fastenings
|  |  | 3.24.5 | Counterweight Sheaves
|  |  | 8.7.3.23.4 | Increase in Working Pressure
CAD 8.7.2.15«1
| CAD 8.7.3.21«1 | « Decrease Deadweight <5% or Increase Deadweight of Car (115 kg or Less) |  |  | Minor B | Minor B
|  | CAD | 8.7.2.15«1
| CAD 8.7.3.21«2 | « Increase Deadweight of Car (>115 kg to 5%) |  |  | Minor A | Minor A
|  | CAD | 8.7.2.15«2
| 8.7.3.22 | Change in Rise or Rated Speed |  |  | Major | -
| 8.7.3.22.1 | Increase or Decrease in Rise |  |  | Major | -
|  |  | 3.25. | Terminal-Stopping Devices
|  |  | 3.4. | Bottom and Top Clearances and Runbys for Cars and Cwts
|  |  | 3.4.1 | Bottom Car Clearance
|  |  | 3.4.2 | Minimum Bottom and Top Car Runby
|  |  | 3.4.3 | Car Top and Bottom Maximum Runby
|  |  | 3.18.2 | Plungers
If decrease in rise is at lowest end then;
|  |  | 2.2.4 | Access to Pits
|  |  | 2.2.5 | Illumination of Pits
|  |  | 2.2.6 | Stop Switches
| 8.7.3.22.2 | Increase in Rated Speed |  |  | Major | -
|  |  | 2.5. | Horizontal Car and Counterweight Clearances
|  |  | 3.4. | Bottom and Top Clearances and Runbys for Cars and Cwts
|  |  | 3.21. | Counterweights
|  |  | 3.22.2(*) | Counterweight Buffers
|  |  | 3.14. | Car: Enclosure, Doors, Gates, Illumination
|  |  | 2.14. | New doors/gates to: Car: Enclosure, Doors, Gates, Illumination
|  |  | 3.17.(*) | Car and Counterweight Safeties
|  |  | 3.16. | Capacity & Loading
|  |  | 3.25. | Terminal-Stopping Devices
|  |  | 3.26.1 | Operating Devices and Control Equipment
|  |  | 3.26.2 | Inspection Operation
|  |  | 3.26.3 | Anti-Creep and Leveling Operation
|  |  | 3.26.4 | Electrical Protective Devices
|  |  | 3.26.5 | Phase-Reversal and Failure Protection
|  |  | 3.26.6 | Control and Operating Circuits
|  |  | 3.20. | Ropes and Rope Connections
| 8.7.3.22.3 | Decrease in Rated Speed |  |  | Major | -
|  |  | 3.4. | Bottom and Top Clearances and Runbys for Cars and Cwts
|  |  | 2.18.2 | Tripping Speeds for Speed Governors
|  |  | 3.16. | Capacity & Loading
|  |  | 3.16.3(b) | Capacity & data plates
|  |  | 2.26.4.1 | Electrical Equipment and Wiring
|  |  | 2.26.4.2 | Drive Machine Controllers for Stopping/Starting/Controlling
| 8.7.3.23 | Hydraulic Equipment |  |  | ò See Below ò
| 8.7.3.23.1 | Alter / Install / Replace |  | Hydraulic Jacks | Major | - | Major
|  |  | 3.18. | Hydraulic Jacks |  |  | see 8.6.3.10.1
| 8.7.3.23.2 | Alter / Install / Replace |  | Plungers | Major | - | Minor A
|  |  | 3.18.1.2 | Roped-Hydraulic Elevator
|  |  | 3.18.2 | Plungers
| 8.7.3.23.3 | Alter / Install / Replace |  | Cylinders | Major | - | Minor A
|  |  | 3.18.3 | Cylinders |  |  | see 8.6.3.10.2
|  |  | 3.18.3 | Cylinder is Altered
|  |  | 3.18.3 | Cylinder is Sleeved | Minor A
|  |  | 3.18.4.1 | Metal Stops and/or Other Means
|  |  | 3.18.1.2 | Roped-Hydraulic Elevator
|  |  | 3.18.2 | Plungers
| 8.7.3.23.4 | Increase in Working Pressure >5% |  |  | Major | -
|  |  | 3.18.(*) | Hydraulic Jacks
|  |  | 3.19.(*) | Valves, Pressure Piping, and Fittings
|  |  | 3.24.1 | Marking Plates
|  |  | 3.24.2 | Tanks
|  |  | 3.24.3 | Atmosphere Storage and Discharge Tanks
|  |  | 3.24.4 | Welding
| 8.7.3.23.5 | Change in Location of Hydraulic Jack |  |  | Major | -
|  |  | Part 3 | Hydraulic Elevators
| 8.7.3.23.6 | Relocation of Hydraulic Machine (Power Unit) |  |  | Minor A | -
|  |  | 3.26.8 | Pressure Switch
| 8.7.3.23.7 | Plunger Gripper |  |  | Minor A | Minor A
|  |  | 3.17.3 | Plunger Gripper
|  |  | 3.1.1(b) | strength of pit floor
|  |  | 3.22.1 | no strike when buffers compressed
CAD
| 8.7.3.23.7 «1 | Removal of Plunger Gripper |  |  | Minor A | -
|  |  | 3.18.3 | Cylinders
|  |  | 3.19.4.7 | Overspeed Valves
|  |  | 3.4.2.1 | Bottom Car Runby
| 8.7.3.24 (a) | Alter / Replace |  | Control Valves | Minor A | - | Minor B
|  |  | 3.19. | Valves, Pressure Piping, and Fittings |  |  | see 8.6.3.11
| 8.7.3.24 (b) | Alter / Replace |  | Relief Valves | Minor A | Minor A | Minor B
|  |  | 3.19. | Valves, Pressure Piping, and Fittings |  |  | see 8.6.3.11
| 8.7.3.24 (b) | Alter / Replace |  | Check Valves | Minor A | Minor A | Minor B
|  |  | 3.19. | Valves, Pressure Piping, and Fittings |  |  | see 8.6.3.11
| 8.7.3.24 (b) | Alter / Replace |  | Pressure Piping or Fittings | Minor A | Minor A | Minor B
|  |  | 3.19. | Valves, Pressure Piping, and Fittings |  |  | see 8.6.3.11
| 8.7.3.25 | Suspension Ropes and Their Connections |  |  | ò See Below ò
| 8.7.3.25.1 | Change in Number of, or Diameter of Ropes |  |  | Major | -
|  |  | 3.20. | Ropes and Rope Connections
PEO to certify retained sheaves w/different ropes are satisfactory
| 8.7.3.25.1 | Change in Material / Grade of Ropes |  |  | Minor A | -
|  |  | 3.20. | Ropes and Rope Connections
PEO to certify retained sheaves w/different ropes are satisfactory
| 8.7.3.25.2 | Addition of Rope Equalizers |  |  | Minor B | Minor B
|  |  | 2.20.5 | Suspension Rope Equalizers
| 8.7.3.26 | Counterweights - Alteration of |  |  | See 8.7.2.22
| 8.7.2.22 | Counterweights |  |  | Minor A | -
| 8.7.2.22.1 |  | Alteration to any part of a cwt except guiding members
|  |  | 2.21. | Counterweights
|  |  | 3.21. | Counterweights
|  |  | 8.7.2.22.2 | Rod Type Counterweights
|  |  | 8.7.2.3 | Location and Guarding of Counterweights
| 8.7.2.22.2 |  | Rod Type Cwt - can retain if:
Minimum of 2 suspension and 2 tie rods
Suspension rods:
|  |  | 2.21.2.1 | Material - Cwt Frames & Rods
|  |  | 2.21.2.3 | Factor of Safety
Tie Rods:
|  |  | 2.21.1.2 | Retention of Weight Sections
| 8.7.2.22.3 |  | Roller or similar guide shoes added |  | mrr |  | mrr
safety jaws cannot touch rails if not activated
| 8.7.3.26 | Counterweights - Addition of |  |  | - | Major
|  |  | 3.4. | Bottom and Top Clearances and Runbys for Cars and Cwts
|  |  | 3.6. | Protection of Spaces below Hoistway
|  |  | 3.14. | Car: Enclosure, Doors, Gates, Illumination
|  |  | 2.14. | Car: Enclosure, Doors, Gates, Illumination
|  |  | 2.14.1.7.1 | car top guard rail to CAD 8.7.2.144
|  |  | 3.15. | Car Frames & Platforms
|  |  | 3.17.2 | Counterweight Safeties
|  |  | 3.18. | Hydraulic Jacks
|  |  | 3.20. | Ropes and Rope Connections
|  |  | 3.21. | Counterweights
|  |  | 8.7.3.3 | Location and Guarding of Counterweights
| 8.7.3.27 | Car Buffers and Bumpers |  |  | Major | - | mrr | Minor B
|  |  | 3.21. | Counterweights
|  |  | 3.22.2(*) | Counterweight Buffers
| 8.7.3.28 | Guide Rails, Supports, and Fastenings (alteration to, or stress increase >5%) |  |  | Major | -
|  |  | 3.23. | Guide Rails, Guide-Rail Supports, and Fastenings
|  |  | 3.28. | Layout Data
| 8.7.3.29 | Alteration to |  | Tanks | Minor B | - | Minor B
|  |  | 3.24. | Hydraulic Machines and Tanks |  |  | see 8.6.3.10.4
| CAD 8.7.3.29«1 | « Addition of Oil Cooler |  |  | Minor B |  | Minor B
|  |  | 8.7.3.8 | Electrical Wiring, Pipes, and Ducts in H/W and M/C rooms
|  |  | 2.7.2 | Maintenance Path and Clearance
|  |  | 3.10. | Guarding of Exposed Auxiliary Equipment
| 8.7.3.30 | Terminal-Stopping Devices |  |  | Minor B | Minor B
|  |  | 3.25. | Terminal-Stopping Devices
| 8.7.3.31 | Operating Devices and Control Equipment |  |  | ò See Below ò
| 8.7.3.31.1 | Top-of-Car Operating Devices |  |  | Minor A | Minor A | mrr | Minor A
|  |  | 3.26.2 | Inspection Operation
| CAD 8.7.3.31«1 | Alteration / Addition of any type of inspection operation |  |  | Minor A | Minor A
|  |  | 2.26.1.4 | Inspection Operation
| CAD 8.7.3.31«2 |  | Addition of Top-of-Car Operating Device (see CAD 3.8.3) |  | - | Minor A
|  |  | 2.26.1.4 | Inspection Operation
8.7.2.15«1,«2
| 8.7.3.31.2 | Car-Leveling or Truck-Zoning Devices |  |  | Minor A | Minor A
|  |  | 3.26.3.2 | Operation in Leveling or Truck Zone
| 8.7.3.31.3 | Alter / Replace |  | Anti-Creep Leveling Device | Minor B | - | Minor B
|  |  | 3.26.3.1 | Anti-Creep Operation |  |  | see 8.6.3.10.5
| CAD 8.7.3.31«3 | « Door By-Pass Switches |  |  | Minor A | Minor A
|  |  | 2.26.1.5 | Inspection Operation with Open Door Circuits
| CAD 8.7.3.31«4 | « Door Monitoring System |  |  | Minor A | Minor A
|  |  | 2.26.5 | System to Prevent Auto Operation w/faulty Door Contacts
| 8.7.3.31.4 | Change in Power Supply |  |  | Major | -
(a) voltage, frequency or # of phases or
(b) AC to DC , DC to AC or
(c) combination of DC & AC, then
electrical to:
|  |  | 3.26.1 | Operating Devices and Control Equipment
|  |  | 3.26.4 | Electrical Protective Devices
|  |  | 3.26.5 | Phase-Reversal and Failure Protection
|  |  | 3.26.6(*) | Control and Operating Circuits
| CAD 8.7.3.31«5 | « Addition of Soft Start |  |  |  | Minor A
|  |  | 2.26.4.1 & 2 | OESC, CSA C22.1 & B44.1 certified
|  |  | 3.26.5 | Phase-Reversal and Failure Protection
| CAD 8.7.3.31«6 | « Addition of Power Efficiency Increasing Device |  |  |  | Minor B
B44.1 certified
|  |  | 2.26.4.1 & 2 | OESC, CSA C22.1 & B44.1 certified
| 8.7.3.31.5 | Controllers
| 8.7.3.31.5(a) | Install / Replace |  | Elevator Controller | Major | - | Major
|  |  | 3.25. | Terminal-Stopping Devices
|  |  | 3.26. | Operating Devices and Control Equipment
|  |  | 3.26.1 | Operating Devices and Control Equipment
|  |  | 3.26.2 | Inspection Operation
|  |  | 3.26.3 | Anti-Creep and Leveling Operation
|  |  | 3.26.4 | Electrical Protective Devices
|  |  | 3.26.5 | Phase-Reversal and Failure Protection
|  |  | 3.26.6 | Control and Operating Circuits
|  |  | 3.26.7 | Recycling Operation for Multiple or Telescopic Plungers
|  |  | 3.26.8 | Pressure Switch
|  |  | 3.26.9 | Low Oil Protection
|  |  | 3.26.10 | Auxiliary Power Lowering Operation
|  | « | 2.7.9.2 | Temperature and Humidity
|  |  | 2.27.2 | when E.P. Is provided
|  |  | 3.27.1 | Phase 1 Emergency Recall Operation after Device Actuation
|  |  | 3.27.2 | Phase 1 Emergency Recall Operation prior to Device Actuation
|  |  | 3.27.3 | Device Acutation at Recall Level
|  |  | 3.27.4 | Device Acutation with Phase II Emergency In-Car in Effect
If FEO previously present or required by OBC;
|  |  | 2.27.3 | Firefighters' Emergency Operation - Automatic Elevators
2.27.3.1 Phase 1 Recall Operation
2.27.3.2 Phase 1 Recall Operation by FAID's
CAD 2.27.3.2.2
2.27.3.3 Phase 2 Emergency In-Car Operation
2.27.3.4 Interruption of Power
2.27.3.5 Multicompartment Elevators
see 8.7.1.2 safety levels shall not be diminished
|  |  | 2.27.4 | FEO: Non Automatic Elevators
|  |  | 2.27.5 | FEO: Automatic Elevators with Designated-Attendant Operation
|  |  | 2.27.6 | FEO: Inspection Operation
|  |  | 2.27.7 | FEO: Operating Procedures
|  |  | 2.27.8 | Switch Keys
|  |  | 2.27.9 | Elevator Corridor Call Station Pictograph
If FEO NOT previously present or required by OBC;
CAD 2.27.3.2.2
2.27.3.1 Provide Phase 1 Manual Recall Operation Only
| CAD 8.7.3.31«7 | Relocation of |  | Elevator Controller (if control wiring disconnected - reconnected) | Major
|  |  | 2.8.2 | Electrical Equipment and Wiring
Electrical testing as per the original design submission tests
| 8.7.3.31.5(b) | Install / Replace |  | Door Controller | Minor A | - | Minor B
|  |  | 2.26.4.1 | Electrical Equipment and Wiring
|  |  | 2.26.4.2 | Drive Machine Controllers for Stopping/Starting/Controlling
| 8.7.3.31.6 | Change in Type of Motion Control |  |  | Major | -
|  |  | 2.11.1(*) | Entrances and Emergency Doors Required
|  |  | 2.11.2 | Types of Entrances
|  |  | 2.11.3 | Closing of Hoistway Doors
|  |  | 2.11.4 | Location of Horizontally Sliding or Swinging H/W Doors
|  |  | 2.11.5 | Projection of Entrances & Equip. Beyond Land'g Sills
|  |  | 2.11.6(*) | Opening of Hoistway Doors
|  |  | 2.11.8 | Weights for Closing or Balancing Doors
|  |  | 2.11.9 | Hoistway Door Locking Devices & Power Operation
|  |  | 2.11.11.8(*) | Hoistway Door Safety Retainers
|  |  | 2.11.12.8 | Pull Straps
|  |  | 2.12.(*) | H/W-Door Locking Devices, Elec. Contacts, H/W Access
2.12.5 Restricted Opening of Hoistway or Car Doors
2.12.6 Hoistway Door Unlocking Devices
2.12.7 Hoistway Access Switches
|  |  | 2.13. | Power Operation of H/W Doors and Car Doors
|  |  | 2.14.(*) | Car: Enclosure, Doors, Gates, Illumination
2.14.1.7 car top railing
|  |  | 8.7.2.27.5(d) | Capacity & Loading
|  |  | 2.17.(*) | Car & Cwt Safeties
|  |  | 2.18.(*) | Speed Governors
|  |  | 3.25. | Terminal Stopping Devices
|  |  | 3.26.(*) | Operating Devices and Control Equipment
|  |  | 2.29. | Identification of Equipment and Floors
|  | « | 2.7.9.2 | Temperature and Humidity
If FEO previously present or required by OBC;
|  |  | 2.27. | Emergency Operation and Signalling Devices
2.27.1 Car Emergency Signalling Devices
2.27.2 Emergency or Standby Power Systems
2.27.3 Firefighters' Emergency Operation: Automatic Elevators
2.27.3.1 Phase 1 Recall Operation
2.27.3.2 Phase 1 Recall Operation by FAID's
CAD 2.27.3.2.2
2.27.3.3 Phase 2 Emergency In-Car Operation
2.27.3.4 Interruption of Power
2.27.3.5 Multicompartment Elevators
see 8.7.1.2 safety levels shall not be diminished
2.27.4 FEO: Non Automatic Elevators
2.27.5 FEO: Automatic Elevators with Designated-Attendant Operation
2.27.6 FEO: Inspection Operation
2.27.7 FEO: Operating Procedures
2.27.8 Switch Keys
If FEO NOT previously present or required by OBC;
CAD 2.27.3.2.2
2.27.3.1 Provide Phase 1 Manual Recall Operation Only
| 8.7.3.31.7 | Change in Type of Operation Control - CPPB, Automatic |  |  | Major | -
|  |  | 2.11.1 | Entrances and Emergency Doors Required
|  |  | 2.11.2 | Types of Entrances
|  |  | 2.11.3 | Closing of Hoistway Doors
|  |  | 2.11.4 | Location of Horizontally Sliding or Swinging H/W Doors
|  |  | 2.11.5 | Projection of Entrances & Equip. Beyond Land'g Sills
|  |  | 2.11.6 | Opening of Hoistway Doors
|  |  | 2.11.7 | Glass in Hoistway Doors
|  |  | 2.11.8 | Weights for Closing or Balancing Doors
|  |  | 2.11.9 | Hoistway Door Locking Devices & Power Operation
|  |  | 2.11.10 | Landing Sill: Guards, Illumination, hinged sills, Tracks
|  |  | 2.11.11 | Entrances, Horizontal Slide Type
|  |  | 2.11.12 | Entrances, Vertical Slide Type
|  |  | 2.11.13 | Entrances, Swing Type
|  |  | 3.11.1 | Protection of Hoistway Landing Openings
|  |  | 3.12.1 | H/W-Door Locking Devices, Elec. Contacts, H/W Access
|  |  | 3.13. | Power Operation of H/W Doors and Car Doors
|  |  | 3.14.(*) | Car: Enclosure, Doors, Gates, Illumination
|  |  | 3.16. | Capacity & Loading
|  |  | 3.25. | Terminal-Stopping Devices
|  |  | 3.26.(*) | Operating Devices and Control Equipment
|  | « | 2.7.9.2 | Temperature and Humidity
|  |  | 3.27. | Emergency Operation and Signaling Devices
3.27.1 PHI Emergency Recall Operation After Device Actuation
(a) low oil protection
(b) plunger follower guide protection
(c) auxiliary power lowering
(d) oil tank temperature shutdown
2.27 Emergency Operation & Signaling Devices
2.27.1 Car Emergency Signalling Devices
2.27.2 Emergency or Standby Power Systems
2.27.3 FEO: Automatic Elevators
CAD 2.27.3.2.2
2.27.4 FEO: Non-Automatic Elevators
2.27.5 FEO: Automatic Elevators w/Attendant
2.27.6 FEO: Inspection Operation
2.27.7 FEO: Operating Procedures
2.27.8 Switch Keys
2.27.9 Elevator Corridor Call Station Pictograph if reqd by OBC
| CAD 8.7.3.31«8 | « Addition of Wander Patient Feature - Change in Operation Control |  |  | Minor B | Minor B
|  |  | 2.11.3.2 | - doors closed when not in use
|  |  | 2.27.3.1.6(l) | - shall not prevent PHI
| CAD 8.7.3.31«9 | « Addition of Restricted Access - Security / Floor Lock Out |  |  | Minor B | Minor B
|  |  | OBC-3.2.6.5(4) | - shall not prevent floor access When on FEO
D.O. Button Remain Operative Under non FEO Conditions, Door Closed When not in Use
|  |  | 2.27.3.1.6(l) | - shall not prevent PHI
|  |  | 2.27.3.3.1(i) | - permit travel to all landings when on PH II
|  |  | 2.11.6.2 | Cannot Lock Out Top& Btm, Designated & Alternate or All Landings in Phase II
|  |  | DR 172/02 | Elevators With Phase II Operation & Floor Button Controlled by Cards/Keys
| 8.7.3.31.8 | Emergency Operation and Signaling Devices
| 8.7.3.31.8(a) | Car Emergency Signaling Devices |  |  | Minor B | Minor B | mrr
|  |  | 2.27.1 | Car Emergency Signaling Devices
| 8.7.3.31.8(b) | Emergency or Standby Power |  |  | Minor B | Minor A
|  |  | 2.27.2 | Emergency Or Standby Power systems
| 8.7.3.31.8(c) | Firefighter's Emergency Operation |  |  | Minor B | Minor A
|  |  | 3.27. | Emergency Operation and Signaling Devices
3.27.1 PHI Emergency Recall Operation After Device Actuation
(a) low oil protection
(b) plunger follower guide protection
(c) auxiliary power lowering
(d) oil tank temperature shutdown
2.27 Emergency Operation & Signaling Devices
2.27.1 Car Emergency Signalling Devices
2.27.2 Emergency or Standby Power Systems
2.27.3 FEO: Automatic Elevators
CAD 2.27.3.2.2
2.27.4 FEO: Non-Automatic Elevators
2.27.5 FEO: Automatic Elevators w/Attendant
2.27.6 FEO: Inspection Operation
2.27.7 FEO: Operating Procedures
2.27.8 Switch Keys
2.27.9 Elevator Corridor Call Station Pictograph if reqd by OBC
CAD
| 8.7.3.31.8«10 | « Emerg. Recall Upgrade - from Manual to Automatic & matching code at time of install |  |  | Minor B
conformance to auto recall based on F.S. at time of install
CAD
| 8.7.3.31.8«11 | « Emerg. Recall Upgrade to comply with a Fire Code Retrofit Order |  |  | Minor B | Minor A
2.27.3 FEO: Automatic Elevators
| 8.7.3.31.9 | Auxiliary Power Lowering Operation |  |  | Minor B | Minor B
|  |  | 3.26.10 | Auxiliary Power Lowering Operation
include testing procedure
| 8.7.3.31.10 | Removal of emergency stop switch on passenger elevators |  |  | Minor B | Minor B
remove all related markings / engravings & provide an in-car stop switch to:
|  |  | 2.26.2.21 | In-car stop switch
|  |  | 2.26.4.3 | Positively Opened Contacts
|  |  | 2.26.9.3.1(a) | single failure does not render In-Car Stop Switch ineffective
|  |  | 3.26.4.2 | deceleration rate <1g, anticreep must still function
| 8.7.3.31.11 | Electrical Protective Devices |  |  | ò See Below ò
| 8.7.2.27.8 | Alteration or Addition of an Electrical Protective Device |  |  | Major | Major | mrr | Major
if device meets 2.26.4.3.2 (PES)
|  |  | 3.26.2 | Electrical Protective Devices - for specified device
| 8.7.2.27.8 | Alteration or Addition of an Electrical Protective Device |  |  | - | Minor A | mrr
if device meets 2.26.4.3.1
|  |  | 3.26.2 | Electrical Protective Devices - for specified device

## 8.7.4 Other
0 | 1 | 2a | 2b | 2c | 3 | 4 | 5 | 6
Conforms to B44 Mark with 'X' | B44-10 Reference Number | Alteration Checklist for Director's Guideline 251-11-r2 Scope of Alteration - B44 - 2010 as amended by CAD 261/13-r1 Part, Section or Requirement |  |  | Type of Alteration Work
[5 empty] | Alteration |  | Replacement with
[5 empty] | Modification Change | Addition | Same | Different Make/Model
|  | Job Reference: |  |  | Type of Submission Required
| 8.7.1.2 | Alterations not specifically covered in 8.7
|  |  | 1.2 | Level of safety shall not be diminished
| 8.7.1.4 | Welding
|  |  | 8.8 | Welding
|  |  | 8.7.1.5 | Design / Weld Engineer
| 8.7.1.7 | Repairs and Replacements
|  |  | 8.6.2 | for repairs
|  |  | 8.6.3 | for replacements
| 8.7.4 | Alterations to Elevators w/other Types of Driving Machines
| 8.7.4.1 | Rack and Pinion Elevators |  |  | Major | -
|  |  | 4.1. | Rack and Pinion Elevators
| 8.7.4.2 | Screw-Column Elevators |  |  | Major | -
|  |  | 4.2. | Screw-Column Elevators
| 8.7.4.3 | Hand Elevators |  |  | Major | -
| 8.7.4.3.1 | Hoistway Enclosures and Machinery Space |  |  | Major | -
|  |  | 4.3.1 | Hoistways, H/W Enclosures, and Related Construction
|  |  | 4.3.4 | Enclosures for Machines and Control Equipment
| 8.7.4.3.2 | Top Car and Counterweight Clearances |  |  | Major | -
|  |  | 4.3.3 | Top Clearances
| 8.7.4.3.3 | Hoistway Entrances |  |  | Major | -
|  |  | 4.3.6 | Hoistway Entrances
|  |  | 4.3.7 | Hoistway Gates for Landing Openings
|  |  | 4.3.8 | Hoistway-Door & Hoistway Gate Locking Devices
| 8.7.4.3.4 | Car Enclosures |  |  | Major | -
|  |  | 4.3.9 | Car Enclosures
|  |  | 4.3.11 | Car Frames and Platforms
| 8.7.4.3.5 | Car Frame and Platform |  |  | Major | -
|  |  | 4.3.11 | Car Frames and Platforms
|  |  | 4.3.12 | Car Compartments
|  |  | 4.3.13 | Cars Counterbalancing One Another
|  |  | 4.3.16 | Suspension Means
| 8.7.4.3.6 | Capacity and Loading |  |  | Major | -
|  |  | 4.3.14.1 | Minimum Rated Load
|  |  | 4.3.14.2 | Capacity Plate
|  |  | 4.3.19.1 | Drive Machine & Sheaves - Factors or Safety
|  |  | 4.3.19.2 | Driving-Machines
|  |  | 4.3.16 | Suspension Means
| 8.7.4.3.7 | Increase in Rise |  |  | Major | -
|  |  | 4.3.3.1 | Top Car Clearances
|  |  | 4.3.3.2 | Top Counterweight Clearance
|  |  | 4.3.15 | Car Safeties
|  |  | 4.3.16 | Suspension Means
| 8.7.4.3.8 | Guide Rails and Fastenings |  |  | Major | -
|  |  | 4.3.18.1 | Guide Rails - Material and Finish
|  |  | 4.3.18.2 | Strength of Rails and Fastenings
|  |  | 4.3.18.3 | Extension of Guide Rails at Top & Bottom of H/W
| 8.7.4.3.9 | Overhead Beams and Supports |  |  | Major | -
|  |  | 4.3.5.1 | Overhead Beams and Supports
|  |  | 4.3.5.2 | Access to Machines and Sheaves
| 8.7.4.3.10 | Power Attachments |  |  | Major | -

## 8.7.5 Special
0 | 1 | 2a | 2b | 2c | 3 | 4 | 5 | 6
Conforms to B44 Mark with 'X' | B44-10 Reference Number | Alteration Checklist for Director's Guideline 251-11-r2 Scope of Alteration - B44 - 2010 as amended by CAD 261/13-r1 Part, Section or Requirement |  |  | Type of Alteration Work
[5 empty] | Alteration |  | Replacement with
[5 empty] | Modification Change | Addition | Same | Different Make/Model
|  | Job Reference: |  |  | Type of Submission Required
| 8.7.1.2 | Alterations not specifically covered in 8.7
|  |  | 1.2 | Level of safety shall not be diminished
| 8.7.1.4 | Welding
|  |  | 8.8 | Welding
|  |  | 8.7.1.5 | Design / Weld Engineer
| 8.7.1.7 | Repairs and Replacements
|  |  | 8.6.2 | for repairs
|  |  | 8.6.3 | for replacements
| 8.7.5 | Alterations to Special Application Elevators
| 8.7.5.1 | Inclined Elevators |  |  | Major | -
|  |  | 5.1. | Inclined Elevators
|  |  |  | compliance to specific 5.1 sections based on alteration scope | variance
| 8.7.5.2 | Limited Use/Limited Application Elevators |  |  | See Electric or Hydraulic Elevator
| CAD 8.7.5.2«1 | « | 8.7.2 | Alterations to Electric Elevator & as modified in Section 5.2
| CAD 8.7.5.2«2 | « | 8.7.3 | Alterations to Hydraulic Elevator & as modified in Section 5.2
| 8.7.5.5 | Power Sidewalk Elevators |  |  | Major | -
| 8.7.5.5.1 | Changes in Electrical Wiring or Electrical Equipment |  |  | Major | -
|  |  | 5.5.1.8 | Equipment in Hoistways & Machine Rooms
| 8.7.5.5.2 | Sidewalk Door |  |  | Major | -
|  |  | 5.5.1.11.2 | Horizontal Openings in Sidewalks and Exterior Areas
|  |  | 5.5.1.11.3 | Hinged Type Swing Sidewalk Doors
|  |  | 5.5.1.11.4 | Vertical Lifting Sidewalk Covers
| 8.7.5.5.3 | Change in Car Enclosure, Car Doors, and Gates |  |  | Major | -
|  |  | 5.5.1.14 | Car Enclosure, Car Doors and Gates, Illumination
| 8.7.5.5.4 | Bow-Irons and Stanchions |  |  | Major | -
|  |  | 5.5.1.15.2 | Bow-Irons and Stanchions
| 8.7.5.5.5 | Increase in Rated Load |  |  | Major | -
|  |  | 5.5.1.16 | Capacity and Loading
|  |  | 5.5.1.18 | Speed Governors
|  |  | 5.5.1.21 | Buffers and Bumpers
|  |  | 5.5.1.25.4 | Maximum Rated Speed
| 8.7.5.5.6 | Increase in Rated Speed |  |  | Major | -
|  |  | 5.5.1.15 | Car Frames and Platforms
|  |  | 5.5.1.16 | Capacity and Loading
|  |  | 5.5.1.19 | Suspension Ropes
|  |  | 5.5.1.22 | Guide Rails
| 8.7.5.5.7 | Existing Driving Machine |  |  | Major | -
|  |  | 5.5.1.8 | Equipment in Hoistways & Machine Rooms
|  |  | 5.5.1.9 | Machinery and Sheave Beams, Supports, and Foundations
|  |  | 5.5.1.23 | Driving Machines and Sheaves
|  |  | 5.5.1.25 | Operating Devices and Control Equipment
| 8.7.5.5.8 | Change in Type of Operating Devices and/or Control Equipment |  |  | Major | -
|  |  | 5.5.1.8 | Equipment in Hoistways & Machine Rooms
|  |  | 5.5.1.25 | Operating Devices and Control Equipment
| 8.7.5.6 | Rooftop Elevators |  |  | Major | -
|  |  | 5.6. | Rooftop Elevators
| 8.7.5.7 | Special Purpose Personnel Elevators |  |  | see CAN/CSA B311

## 8.7.6.1 Esc
0 | 1 | 2a | 2b | 2c | 3 | 4 | 5 | 6
Conforms to B44 Mark with 'X' | B44-10 Reference Number | Alteration Checklist for Director's Guideline 251-11-r2 Scope of Alteration - B44 - 2010 as amended by CAD 261/13-r1 Part, Section or Requirement |  |  | Type of Alteration Work
[5 empty] | Alteration |  | Replacement with
[5 empty] | Modification Change | Addition | Same | Different Make/Model
|  | Job Reference: |  |  | Type of Submission Required
| 8.7.1.2 | Alterations not specifically covered in 8.7
|  |  | 1.2 | Level of safety shall not be diminished
| 8.7.1.4 | Welding
|  |  | 8.8 | Welding
|  |  | 8.7.1.5 | Design / Weld Engineer
| 8.7.1.7 | Repairs and Replacements
|  |  | 8.6.2 | for repairs
|  |  | 8.6.3 | for replacements
| 8.7.6.1 | Alterations to Escalators
| 8.7.6.1.1 | Change to component parts |  |  | mrr | - | mrr
8.6.12.4.1.1 Replacement parts or components
8.6.12.4.1.2 Quality of Work
| 8.7.6.1.1 | Addition of Components or Devices |  |  | see 8.7.6.1 |  | -
see applicable 8.7.6.1 requirements for that device
| 8.7.6.1.2 (a) | Relocation of Escalator |  |  | New | -
|  |  | 6.1. | Escalators
| 8.7.6.1.2 (b) | Repositioning of Escalator |  |  | Major
| CAD 3.18 | « Repositioning of Escalator (within the same building)
|  |  | 6.1.3.3.11 | Guard at ceiling intersection
|  |  | 6.1.3.3.12 | AntiSlide Devices
|  |  | 6.1.3.3.13 | Deck Barricades
|  |  | 6.1.3.4.3 | Guards
|  |  | 6.1.3.6.3 | Adjacent Floor Surfaces
|  |  | 6.1.3.6.4 | Safety Zone
|  |  | 6.1.3.12 | Headroom
|  |  | 6.1.3.13 | Welding
|  |  | 6.1.6.9 | Signs
|  |  | 6.1.7.4.1 | Electrical equipment
|  |  | 8.7.6.1.3 | Protection of Floor Openings
| 8.7.6.1.3 | Protection of Floor Openings |  |  | Minor A | -
|  |  | 6.1.1.1 | Protection Required
| 8.7.6.1.4 | Protection of Trusses and Machinery Spaces Against Fire |  |  | Minor A | -
|  |  | 6.1.2.1 | Protection Required
| 8.7.6.1.5 | Construction Requirements
| 8.7.6.1.5(a) | Construction Requirements - Angle of Inclination |  |  | Major | -
| 8.7.6.1.5(b) | Construction Requirements - Geometry |  |  | Major | -
|  |  | 6.1.3.2 | Geometry
| 8.7.6.1.5(c) | Any Alteration to the Balustrades |  |  | Minor A | Minor A
|  |  | 6.1.3.3 | Balustrades
|  |  | 6.1.3.3.1 | Construction
|  |  | 6.1.3.3.2 | Strength
|  |  | 6.1.3.3.3 | Use of Glass or Plastic
|  |  | 6.1.3.3.4 | Interior Low Deck
|  |  | 6.1.3.3.5 | Loaded Gap between Skirt & Step
|  |  | 6.1.3.3.6 | Skirt Panels
|  |  | 6.1.3.3.7 | Dynamic Skirt Panels
|  |  | 6.1.3.3.8 | Dynamic Skirt Panel Loaded Gap
|  |  | 6.1.3.3.9 | Step/Skirt Performance Index
|  |  | 6.1.3.3.10 | Skirt Deflector Devices
|  |  | 6.1.3.3.11 | Guard at ceiling intersection
|  |  | 6.1.3.3.12 | AntiSlide Devices
|  |  | 6.1.3.3.13 | Deck Barricades
| 8.7.6.1.5(d) | Deflector Devices |  |  | Minor B |  | mrr
|  |  | 6.1.3.3.10 | Skirt Deflector Devices
| 8.7.6.1.6 | Handrails or Handrail System |  |  | Minor A | -
|  |  | 6.1.3.2.2 | Geometry - Handrail
|  |  | 6.1.3.4.1 | Handrails - Type Required
|  |  | 6.1.3.4.2 | Extension Beyond Combplate
|  |  | 6.1.3.4.3 | Guards (hand or finger)
|  |  | 6.1.3.4.4 | Handrails - Splicing
|  |  | 6.1.3.4.6 | Handrail Clearance
|  |  | 6.1.6.3.12 | Handrail Entry Device
|  |  | 6.1.6.4 | Handrail Speed Monitoring Device
| CAD 8.7.6.1«1 | « Addition of Handrail Advertising |  |  | mrr | variance
Variance to 6.1.6.9.2
| 8.7.6.1.7 | Step System - any alteration to the step system |  |  | Major | - | mrr | Minor B
|  |  | 6.1.3.3.5 | Loaded Gap Between Skirt & Step
|  |  | 6.1.3.5 (*) | Steps
|  |  | 6.1.3.6 | Entrance and Egress Ends
|  |  | 6.1.3.8 | Step Wheel Tracks
|  |  | 6.1.3.9.4 | Step
|  |  | 6.1.3.10.4 | Factor of Safety - Steps
|  |  | 6.1.3.11 | Chains
|  |  | 6.1.6.3.3 | Broken Step-Chain Device
|  |  | 6.1.6.3.9 | Step Upthrust Device
|  |  | 6.1.6.3.11 | Step Level Device
|  |  | 6.1.6.3.14 | Step Lateral Displacement Device
|  |  | 6.1.6.5 | Missing Step Device
| 8.7.6.1.8 | Combplates |  |  | Minor A | -
|  |  | 6.1.6.3.13 | Comb-Step Impact Devices
| 8.7.6.1.9 | Trusses and Girders |  |  | Major | -
|  |  | 8.7.1.4 | Welding
|  |  | 6.1.3.7 | Trusses of Girders
|  |  | 6.1.3.9.1 | Structural Load
|  |  | 6.1.3.10.1 | Factor of Safety - Trusses and Supporting Structures
| 8.7.6.1.9 | New Escalator into Existing Trusses |  |  | New | -
|  |  | 6.1. | Escalators
| 8.7.6.1.10 | Step Wheel Tracks |  |  | Major | -
|  |  | 6.1.3.8 | Step Wheel Tracks
|  |  | 6.1.3.9.4 | Step
|  |  | 6.1.3.10.1 | Factor of Safety - Trusses and Supporting Structures
|  |  | 8.7.1.4 | Welding
| 8.7.6.1.11 | Rated Load and Speed |  |  | Major | -
|  |  | 6.1. | Escalators
| 8.7.6.1.12 | Driving Machine, Motor, and Brake
| 8.7.6.1.12(a) | Driving Machine |  |  | Major | -
|  |  | 6.1.3.9.2 | Machinery
|  |  | 6.1.3.10.3 | Factor of Safety - Power Transmission Parts
|  |  | 6.1.4.1 | Limits of Speed
|  |  | 6.1.5.1 | Connection Between Driving Machine and Main Drive Shaft
|  |  | 6.1.5.2 | Driving Motor
|  |  | 6.1.5.3.1 | Escalator Driving-Machine Brake
|  |  | 6.1.5.3.2 | Main Drive Shaft Brake
|  |  | 6.1.6.3.4 | Broken Drive-Chain Device
|  |  | 6.1.6.3.8 | reversal Stop Device
| 8.7.6.1.12(b) | Driving Motor |  |  | Major | -
|  |  | 6.1.3.9.2 | Machinery
|  |  | 6.1.3.10.3 | Factor of Safety - Power Transmission Parts
|  |  | 6.1.4.1 | Limits of Speed
|  |  | 6.1.5.2 | Driving Motor
|  |  | 6.1.5.3.1 | Escalator Driving-Machine Brake
|  |  | 6.1.5.3.2 | Main Drive Shaft Brake
|  |  | 6.1.6.3.2 | Speed Governor
|  |  | 6.1.6.3.8 | reversal Stop Device
|  |  | 6.1.6.3.10 | Disconnected Motor Safety Device
| 8.7.6.1.12(c) | Machine Brake |  |  | Major | -
|  |  | 6.1.3.9.3 | Brake
|  |  | 6.1.3.10.2 | Factor of Safety - Driving Machine Parts
|  |  | 6.1.5.3.1 | Escalator Driving-Machine Brake
| 8.7.6.1.13 | Operating and Safety Devices |  |  | Minor A | Minor A
|  |  | 6.1.6 | Operating and Safety Devices (for that device)
| CAD 8.7.6.1«2 | « Removal of step demarcation lights |  |  | Minor A | - | -
|  |  | 6.1.3.3.5 | Loaded Gap Between Skirt & Step
|  |  | 6.1.3.5.4 | Clearance between Steps
|  |  | 6.1.3.5.5 | Slotting of Steps and Treads
|  |  | 6.1.3.5.6 | Step Demarcation
|  |  | 6.1.3.6.2 | Distinction Between Comb and Step
| 8.7.6.1.14 | Lighting, Access, and Electrical Work |  |  | Minor B | Minor B
|  |  | 6.1.7 | Lighting, Access, and Electrical Work
| 8.7.6.1.15 | Entrance and Egress |  |  | Major | -
|  |  | 6.1.3.6.1 | Combplates
|  |  | 6.1.3.6.2 | Distinction Between Comb and Step
|  |  | 6.1.3.6.3 | Adjacent Floor Surfaces
|  |  | 6.1.3.6.4 | Safety Zone
| 8.7.6.1.16 | Controller |  |  | Major | - | -
|  |  | 6.1.6.10 | Control and Operating Circuits
|  |  | 6.1.6.11 | Electrically Power Safety Devices
|  |  | 6.1.6.12 | Installation of Capacitors.. To Make EPD's Ineffective
|  |  | 6.1.6.13 | Completion of Maintenance Circuits
|  |  | 6.1.6.14 | Escalator Manual Reset
|  |  | 6.1.6.15 | Contractors and Relays for Use in Critical Operating Circuits
| CAD 8.7.6.1«3 | « Controller - Replacement of |  |  | - | - | Major
|  |  | 8.7.6.1.16 | Controller
| CAD 8.7.6.1«4 | Relocation of |  | Controller (if control wiring disconnected - reconnected) | Major
|  |  | 2.8.2 | Electrical Equipment and Wiring
Electrical testing as per the original design submission tests
| CAD 8.7.6.1«5 | « Addition of Soft start |  |  | - | Minor A
for control systems built to B44-00 and later
|  |  | 6.1.7.4 | Electrical Equipment and Wiring
|  |  | 6.1.6.10.1 | Occurrence of a single ground
|  |  | 6.1.6.10.2 | Redundancy to be checked
|  |  | 6.1.6.10.3 | Motors with Static control
for control systems built prior to B44-00
|  |  | 6.1.7.4 | Electrical Equipment and Wiring
| CAD 8.7.6.1«6 | « Addition of Power Efficiency Increasing Device |  |  | - | Minor B
B44.1 certified
|  |  | 2.26.4.1 & 2 | OESC, CSA C22.1 & B44.1 certified

## 8.7.6.2 MW
0 | 1 | 2a | 2b | 2c | 3 | 4 | 5 | 6
Conforms to B44 Mark with 'X' | B44-10 Reference Number | Alteration Checklist for Director's Guideline 251-11-r2 Scope of Alteration - B44 - 2010 as amended by CAD 261/13-r1 Part, Section or Requirement |  |  | Type of Alteration Work
[5 empty] | Alteration |  | Replacement with
[5 empty] | Modification Change | Addition | Same | Different Make/Model
|  | Job Reference: |  |  | Type of Submission Required
| 8.7.1.2 | Alterations not specifically covered in 8.7
|  |  | 1.2 | Level of safety shall not be diminished
| 8.7.1.4 | Welding
|  |  | 8.8 | Welding
|  |  | 8.7.1.5 | Design / Weld Engineer
| 8.7.1.7 | Repairs and Replacements
|  |  | 8.6.2 | for repairs
|  |  | 8.6.3 | for replacements
| 8.7.6.2 | Alterations to Moving Walks
| 8.7.6.2.1 | Change to component parts |  |  | mrr | - | mrr
8.6.12.4.1.1 Replacement parts or components
8.6.12.4.1.2 Quality of Work
| 8.7.6.2.1 | Addition of Components or Devices |  |  | see 8.7.6.2 |  | -
see applicable 8.7.6.2 requirements for that device
| 8.7.6.2.2 | Relocation of Moving Walk |  |  | New | -
|  |  | 6.2. | Moving Walks
| 8.7.6.2.3 | Protection of Floor Openings |  |  | Minor A | -
|  |  | 6.2.1.1 | Protection Required
| 8.7.6.2.4 | Protection of Trusses and Machinery Spaces Against Fire |  |  | Minor A | -
|  |  | 6.2.2.1 | Protection of Supports - Protection Required
| 8.7.6.2.5 | Construction Requirements - Angle of Inclination |  |  | Major | -
|  |  | 6.2. | Moving Walks
| 8.7.6.2.5 | Construction Requirements - Geometry |  |  | Major | -
|  |  | 6.2.3.2 | Geometry
| 8.7.6.2.5 | Construction Requirements - Balustrades |  |  | Minor A | Minor A
|  |  | 6.2.3.3 | Balustrades
| 8.7.6.2.6 | Handrails |  |  | Minor A | -
|  |  | 6.2.3.2.3 | Geometry - Handrail
|  |  | 6.2.3.4 | Handrails
|  |  | 6.2.6.3.10 | Handrail Entry Device
|  |  | 6.2.6.4 | Handrail Speed Monitoring Device
| 8.7.6.2.7 | Treadway System |  |  | Major | -
|  |  | 6.2.3.2.3 | Geometry - Handrail
|  |  | 6.2.3.3.5 | Skirtless Balustrade
|  |  | 6.2.3.3.6 | Skirt Panels
|  |  | 6.2.3.5 | Pallet-Type Treadway
|  |  | 6.2.3.6(*) | Belt-Type Treadway
|  |  | 6.2.3.8 | Entrance and Egress Ends
|  |  | 6.2.3.9 | Supporting Structure
|  |  | 6.2.3.10.4 | Pallet
|  |  | 6.2.3.11.4 | Pallet Factor of Safety
|  |  | 6.2.3.11.5 | Belt Factor of Safety
|  |  | 6.2.3.12 | Chains
|  |  | 6.2.6.3.3 | Broken Treadway Device
|  |  | 6.2.6.5 | Missing Pallet Device
|  |  | 6.2.6.3.9 | Pallet Level Device
| 8.7.6.2.8 | Combplates |  |  | Minor A | -
|  |  | 6.2.3.8 | Entrance and Egress Ends
|  |  | 6.2.6.3.11 | Comb-Pallet Impact Devices
| 8.7.6.2.9 | Trusses and Girders |  |  | Major | -
|  |  | 8.7.1.4 | Welding
|  |  | 6.2.3.9 | Supporting Structure
|  |  | 6.2.3.10.1 | Structural Load
|  |  | 6.2.3.12.1 | Trusses & Supports based on max static load
| 8.7.6.2.9 | New Moving Walk into Existing Truss |  |  | New | -
|  |  | 6.2. | Moving Walks
| 8.7.6.2.10 | Track System |  |  | Major | -
|  |  | 6.2.3.9 | Supporting Structure
|  |  | 6.2.3.10 | Rated Load
|  |  | 6.2.3.11.1 | Trusses & Supports based on max static load
|  |  | 8.7.1.4 | Welding
| 8.7.6.2.11 | Rated Load and Speed |  |  | Major | -
|  |  | 6.2. | Moving Walks
| 8.7.6.2.12 | Driving Machine |  |  | Major | -
|  |  | 6.2.3.10.2 | Machinery Load
|  |  | 6.2.3.11.2 | Factor of Safety for Drive Machine Parts
|  |  | 6.2.3.11.3 | Factor of Safety for Power Transmission members
|  |  | 6.2.3.14 | V-Belt Drives
|  |  | 6.2.3.15 | Headroom
|  |  | 6.2.4 | Rated Speed
|  |  | 6.2.5.1 | Connection Between Driving Machine and Main Drive Shaft
|  |  | 6.2.5.3.1 | Moving Walk Driving-Machine Brakes
|  |  | 6.2.5.3.2 | Main Drive Shaft Brake
|  |  | 6.2.6.3.4 | Broken Drive-Chain Device
|  |  | 6.2.6.3.8 | Disconnected Motor Safety Device
| 8.7.6.2.12 | Drive Motor |  |  | Major | -
|  |  | 6.2.3.10.2 | Machinery Load
|  |  | 6.2.3.11.2 | Factor of Safety for Drive Machine Parts
|  |  | 6.2.3.11.3 | Factor of Safety for Power Transmission members
|  |  | 6.2.4 | Rated Speed
|  |  | 6.2.5.2 | Driving Motor
|  |  | 6.2.5.3.1 | Moving Walk Driving-Machine Brakes
|  |  | 6.2.6.3.2 | Speed Governor
|  |  | 6.2.6.3.7 | Reversal Stop Device
|  |  | 6.2.6.3.8 | Disconnected Motor Safety Device
| 8.7.6.2.12 | Machine Brake |  |  | Major | -
|  |  | 6.2.3.10.3 | Brake
|  |  | 6.2.3.11.2 | Factor of Safety for Drive Machine Parts
|  |  | 6.2.3.11.3 | Factor of Safety for Power Transmission members
|  |  | 6.2.5.3.1 | Moving Walk Driving-Machine Brakes
|  |  | 6.2.5.3.2 | Main Drive Shaft Brake
| 8.7.6.2.13 | Operating and Safety Devices |  |  | Minor A | Minor A
|  |  | 6.2.6 | Operating and Safety Devices (for that device)
| 8.7.6.2.14 | Lighting, Access, and Electrical Work |  |  | Minor B | Minor B
|  |  | 6.2.7 | Lighting, Access, and Electrical Work
| 8.7.6.2.15 | Controller - Installed as part of an alteration |  |  | Major | - | -
|  |  | 6.2.6.9 | Control and Operating Circuits
|  |  | 6.2.6.10 | Electrically Power Safety Devices
|  |  | 6.2.6.11 | Installation of Capacitors.. To Make EPD's Ineffective
|  |  | 6.2.6.12 | Completion of Maintenance Circuits
|  |  | 6.2.6.13 | Moving Walk Manual Reset
|  |  | 6.2.6.14 | Contractors and Relays for Use in Critical Operating Circuits
| CAD 8.7.6.2«1 | « Controller - Replacement of |  |  | - | - | Major
|  |  | 8.7.6.1.16 | Controller
| CAD 8.7.6.2«2 | Relocation of |  | Controller (if control wiring disconnected - reconnected) | Major
|  |  | 2.8.2 | Electrical Equipment and Wiring
Electrical testing as per the original design submission tests
| CAD 8.7.6.2«3 | « Addition of Soft start |  |  | - | Minor A
for control systems built to B44-00 and later
|  |  | 6.1.7.4 | Electrical Equipment and Wiring
|  |  | 6.1.6.10.1 | Occurrence of a single ground
|  |  | 6.1.6.10.2 | Redundancy to be checked
|  |  | 6.1.6.10.3 | Motors with Static control
for control systems built prior to B44-00
|  |  | 6.1.7.4 | Electrical Equipment and Wiring
| CAD 8.7.6.2«4 | « Addition of Power Efficiency Increasing Device |  |  | - | Minor B
B44.1 certified
|  |  | 2.26.4.1 & 2 | OESC, CSA C22.1 & B44.1 certified

## 8.7.7 DW Matl
0 | 1 | 2a | 2b | 2c | 3 | 4 | 5 | 6
Conforms to B44 Mark with 'X' | B44-10 Reference Number | Alteration Checklist for Director's Guideline 251-11-r2 Scope of Alteration - B44 - 2010 as amended by CAD 261/13-r1 Part, Section or Requirement |  |  | Type of Alteration Work
[5 empty] | Alteration |  | Replacement with
[5 empty] | Modification Change | Addition | Same | Different Make/Model
|  | Job Reference: |  |  | Type of Submission Required
| 8.7.1.2 | Alterations not specifically covered in 8.7
|  |  | 1.2 | Level of safety shall not be diminished
| 8.7.1.4 | Welding
|  |  | 8.8 | Welding
|  |  | 8.7.1.5 | Design / Weld Engineer
| 8.7.1.7 | Repairs and Replacements
|  |  | 8.6.2 | for repairs
|  |  | 8.6.3 | for replacements
| 8.7.7 | Alterations to Dumbwaiters and Material Lifts
| 8.7.7.1 | Dumbwaiters and Material Lifts Without Automatic Transfer Devices |  |  | Major | -
|  | Alteration to a Power and Hand Dumbwaiters |  |  | Major | -
|  |  | 7.1. | Power and Hand Dumbwaiters
|  |  | 7.2. | Electric and Hand Dumbwaiters
|  |  | 7.3. | Hydraulic Dumbwaiters
|  | Alteration to a Material Lifts |  |  | Major | -
|  |  | 7.4. | Material Lifts
| CAD 3.9.2 | Lock and Contact upgrade to Interlock |  |  | Minor A | Minor A
CAD 3.9.2
|  |  | 7.4.14* | Hoistway Door Locking Devices
| 8.7.7.1.1 | General Alterations other than 8.7.7.1.2 |  |  | Major | -
|  |  | Part 7 | Dumbwaiters and Material Lifts
| 8.7.7.1.2 | Increase in Rated Load |  |  | Major | -
|  |  | 7.2.(*) | Electric and Hand Dumbwaiters w/o Transfer Devices
|  |  | 7.3.(*) | Hydraulic Dumbwaiters w/o Transfer Devices
|  |  | 7.4. | Material Lifts
|  |  | 7.5. | Electric Material Lifts
|  |  | 7.6. | Hydraulic Material Lifts
| 8.7.7.2 | Addition of Automatic Transfer Device |  |  | Major | -
|  |  | Part 2 | Electric Elevators
|  |  | Part 3 | Hydraulic Elevators
| 8.7.7.3.1 | Material Lifts and Dumbwaiters With Automatic Transfer Devices |  |  | N/A | N/A
exempt if requirements of CAD 2.3(j) are met
| 8.7.7.3.2 | Material Lifts and Dumbwaiters - remove Transfer Device |  |  | New | -
|  |  | 7.1. to 7.3. | for Dumbwaiters
|  |  | 7.4. to 7.6 | Material Lifts w/o Transfer Devices
| 8.7.7.3.3 | Material Lifts altered to an Elevator |  |  | New | -
|  |  | Part 2 | Electric Elevators
|  |  | Part 3 | Hydraulic Elevators
| 8.7.7.3.4 | Material Lift or Dumbwaiter w/ Transfer Device Altered to a D/W |  |  | New | -
|  |  | 7.1. | Power and Hand Dumbwaiters w/Auto Transfer Devices
|  |  | 7.2. | Electric and Hand Dumbwaiters w/o Transfer Devices
|  |  | 7.3. | Hydraulic Dumbwaiters w/o Transfer Devices
Alterations to Freight Platform Lifts
| CAD 8.7.7«1 | « Alteration to a Type 'A' Freight Platform Lift |  |  | Major | -
|  |  | 7.4. | as applicable to Material Lifts Type 'B' 
|  |  | 7.5. | as applicable to Material Lifts Type 'B' 
|  |  | 7.6. | as applicable to Material Lifts Type 'B' 
 excluding requirements related to in-car operating devices & Riders
| CAD 3.9.2 | Lock and Contact upgrade to Interlock |  |  | Minor A | Minor A
CAD 3.9.2
|  |  | 7.4.14* | Hoistway Door Locking Devices
| CAD 8.7.7«2 | « Alteration to a Type 'B' Freight Platform Lift |  |  | Major | -
|  |  | 7.4. | as applicable to Material Lifts Type 'B'
|  |  | 7.5. | as applicable to Material Lifts Type 'B'
|  |  | 7.6. | as applicable to Material Lifts Type 'B'
| CAD 3.9.2 | Lock and Contact upgrade to Interlock |  |  | Minor A | Minor A
CAD 3.9.2
|  |  | 7.4.14* | Hoistway Door Locking Devices